## Sheet1
Table E-10 Power Requirements of Medical Equipments in a Trauma Hospital
Floor | Dept. | Room | Service | Room/ Bed | Equipment | Qty. | Unit Load | Total | Load on UPS
GF | OTs OT-I & II |  | General Theatre | 2 | DT Table | 2 | 400 | 800 | 800
[5 empty] | OT Light | 2 | 400 | 800 | 800
[5 empty] | Defibrillator | 2 | 70 | 140 | 800
[5 empty] | Anaesthesia (Work Station) | 2 | 200 | 400 | 240
[5 empty] | Monitor | 2 | 120 | 240 | 1600
[5 empty] | EI Cautery | 2 | 800 | 1600 | 1000
[5 empty] | C- Arm | 1 | 7000 | 7000 | 1100
[5 empty] | Ligasure | 2 | 500 | 1000 | 500
[5 empty] | Har. Scalper | 2 | 550 | 1100 | 6000
[5 empty] | Argon Caulery | 1 | 500 | 500 | 1000
[5 empty] | Endoscopic (Set + Trolley ) | 2 | 3000 | 6000
[5 empty] | Operating Microscope | 2 | 500 | 1000
[5 empty] | Syringe Pumps | 6 | 20 | 120
[5 empty] | Flash Sterilizer | 1 | 2500 | 2500
[5 empty] | Body Warmer | 2 | 1200 | 2400
GF | ECG Room | 004 | ECG | 1 | ECG Machine | 2 | 50 | 100 | 100
GF | X- Ray Room | 009 | X- Ray | 1 | X- Ray 200 MA | 1 | 30000 | 30000
GF | Triage | 023 | Resuscitation + Observation | 26 Beds | Monitors | 26 | 120 | 3120 | 3120
[5 empty] | Defibrillator | 13 | 70 | 910
[5 empty] | Suction Machine | 13 | 750 | 9750
GF | Diagnostics | 055 057 | X- Ray | 2 | X- Ray Machines 500/800 MA | 1 | 50000 | 50000
[6 empty] | 1 | 70000 | 70000
|  | 054 | Ultrasound | 1 | Ultrasound Machine | 1 | 2000 | 2000 | 2000
|  | 052 | CT Scan | 1 | CT Scan | 1 | 90000 | 90000 | Vendor UPS
[5 empty] | Defibrillator | 1 | 70 | 70
|  | 053 | MRI |  | MRI | 1 | 90000 | 90000 | Vendor UPS
[5 empty] | MRI Chiller | 1 | 30000 | 30000
|  | 052 | Console CT |  | Console + Comptr. | 1 | 250 | 250 | Vendor UPS
|  | 053 | Console MRI |  | Console + Comptr. | 1 | 250 | 250 | Vendor UPS
FF | CCU | 125 | Nursing Station | 1 | Central Station | 1 | 250 | 250 | 250
|  |  | Beds. | 18 | Monitor @1.5 | 27 | 120 | 3240 | 250
[5 empty] | Ventilator | 12 | 500 | 6000 | 3240
[5 empty] | Pulse Oximeter | 4 | 70 | 280 | 6000
[5 empty] | Syringe Pumps | 24 | 20 | 480
[5 empty] | Infusion Pumps | 12 | 20 | 240
[5 empty] | Suction Machine | 3 | 750 | 2250
[5 empty] | Portable U/S | 1 | 2000 | 2000 | 2000
[5 empty] | Body Warmer | 4 | 1200 | 4800
[5 empty] | Defibrillator | 2 | 70 | 140
[5 empty] | ECG Machine | 2 | 50 | 100
[5 empty] | IABP | 2 | 400 | 800 | 800
[5 empty] | Nebulizer | 4 | 25 | 100 | 100
FF | MICU | 128 | ICU | Beds | Central Station | 1 | 500 | 500 | 500
|  |  |  | 16 | Monitor | 16 | 120 | 1920 | 1920
[5 empty] | Ventilator | 8 | 500 | 4000 | 4000
[5 empty] | Defibrillator | 2 | 70 | 140
[5 empty] | ECG Machine | 2 | 50 | 100
[5 empty] | Pulse Oximeter | 4 | 70 | 280
[5 empty] | Syringe Pump | 16 | 20 | 320
[5 empty] | Infusion Pumps | 3 | 20 | 60
[5 empty] | Nebulizer | 2 | 25 | 50
[5 empty] | Suction Machine | 2 | 750 | 1500
[5 empty] | Body Warmer | 4 | 1200 | 4800
2F | Blood Bank | 224 | Blood Bank |  | Plasma Pheresis | 1 | 500 | 500 | 500
[5 empty] | Blood Mixer & Collector with Scale and auto Shut Off | 5 | 120 | 600 | 600
[5 empty] | Tube Sealer Thermal | 1 | 200 | 200
[5 empty] | Needle Destroyer | 2 | 250 | 500
[5 empty] | Blood Bank Refrigerator | 1 | 400 | 400
[5 empty] | Centrifuge Table Model | 2 | 350 | 700
[5 empty] | Water Bath/ Air Bath (370 C to 570 C ) | 1 | 150 | 150
[5 empty] | Incubator With Thermostatic Control | 1 | 1500 | 1500
[5 empty] | Microscopers Binocular. | 2 | 50 | 100
[5 empty] | Medical Refrigerator with Temp. Display. | 1 | 400 | 400
[5 empty] | Automatic Red Cell Washer | 1 | 200 | 200
[5 empty] | Elisa Reaer | 1 | 200 | 200 | 200
[5 empty] | Centrifuge | 1 | 350 | 350
[5 empty] | Incubator with Temp Control. | 1 | 1000 | 1000
[5 empty] | VDRL Shaker | 1 | 100 | 100
[5 empty] | Medical Refrigerator | 1 | 400 | 400
[5 empty] | U/S Cleaner | 1 | 2000 | 2000
[5 empty] | Auto Clave | 1 | 2000 | 2000
[5 empty] | Hot Air Oven | 1 | 1500 | 1500
[5 empty] | Deep Freeze- 35 -700 C. | 1 | 450 | 450
[5 empty] | Deep Freeze 70 | 1 | 800 | 800
FF | Pathology | 227 |  |  | Water Bath | 6 | 200 | 1200
| Biochemistry | 228 |  |  | Autoclave | 2 | 2000 | 4000
[5 empty] | Automatic Chemistry Analyser | 1 | 3000 | 3000 | 3000
[5 empty] | Blood Gas Analyser | 1 | 200 | 200 | 200
[5 empty] | Electrolyte Analyser | 1 | 250 | 250 | 250
[5 empty] | Immuno Assay System | 1 | 3000 | 3000 | 3000
[5 empty] | Blood Cell Counter | 1 | 500 | 500 | 500
[5 empty] | Balance Semi Micro | 2 | 50 | 100 | 100
[5 empty] | Balance Micro | 1 | 50 | 50
[5 empty] | Vertex Mixer | 2 | 50 | 100
[5 empty] | Constant Temp. Water Bath | 2 | 200 | 400
[5 empty] | Incubator with Thermostat | 2 | 1500 | 3000
[5 empty] | Hot Air Oven | 2 | 500 | 1000
[5 empty] | Magnetic Stirrer | 2 | 250 | 500
[5 empty] | Colorimeter | 4 | 100 | 400 | 400
[5 empty] | Refrigerator | 3 | 400 | 1200
[5 empty] | Flame Photometer. | 2 | 100 | 200
[5 empty] | Clinical centrifuge | 4 | 350 | 1400
[5 empty] | pH-meter | 3 | 50 | 150
[5 empty] | Microscope | 6 | 50 | 300
[5 empty] | Electrophoresis | 6 | 50 | 300
[5 empty] | Spectrophotometer | 1 | 100 | 100 | 100
[5 empty] | Binocular research microscope | 2 | 200 | 400 | 400
[5 empty] | Rotary microtome | 1 | 300 | 300 | 300
[5 empty] | Paraffin bath | 2 | 200 | 400 | 400
[5 empty] | Electric vacuum bath | 2 | 300 | 600 | 600
[5 empty] | Autoclave | 2 | 2000 | 4000
[5 empty] | 570 C water bath | 1 | 500 | 500
[5 empty] | Rectangular water bath | 1 | 800 | 800
[5 empty] | Centrifuge | 1 | 350 | 350
[5 empty] | Colorimeter | 1 | 100 | 100
[5 empty] | Auto tissue processor | 1 | 500 | 500 | 500
[5 empty] | Water bath Electric | 2 | 250 | 500
[5 empty] | Balance Chemical | 2 | 50 | 100
[5 empty] | PH meter Electric | 1 | 50 | 50
[5 empty] | Binocular Research Microscope | 1 | 200 | 200 | 200
[5 empty] | Electrophoresis (Vertical + Horizontal) | 2 | 50 | 100
[5 empty] | Microscope high power, oil immersion | 10 | 50 | 500
[5 empty] | Centrifuge | 3 | 350 | 1050
[5 empty] | PH meter Electric | 1 | 50 | 50
[5 empty] | Incubator | 1 | 1500 | 1500
[5 empty] | Water bath Electric | 2 | 200 | 400
[5 empty] | Incubator Large | 4 | 1500 | 6000
[5 empty] | Autoclave | 2 | 2000 | 4000
[5 empty] | Hot Air Sterilizer | 2 | 500 | 1000
[5 empty] | Refrigerator | 3 | 400 | 1200
[5 empty] | Centrifuge | 2 | 350 | 700
[5 empty] | Refrigerated Centrifuge | 1 | 1000 | 1000
[5 empty] | Microscope Arc Lamp | 1 | 50 | 50
[5 empty] | Electrophoresis Complete | 1 | 50 | 50
[5 empty] | BOD Incubator | 1 | 1000 | 1000
[5 empty] | Laminator Flow Table | 1 | 1000 | 1000
[5 empty] | VDRL Shaker | 2 | 100 | 200
[5 empty] | 560 C Water Bath | 1 | 100 | 100
[5 empty] | 20 0 C Deep Freezer | 1 | 500 | 500
[5 empty] | Elisa Reader + Washer | 1 | 200 | 200 | 200
[5 empty] | Binocular Microscope | 2 | 200 | 400 | 400
[5 empty] | Autoclave | 1 | 2000 | 2000
[5 empty] | U/s Cleaner | 1 | 2000 | 2000
[5 empty] | Hot Air Oven | 1 | 1500 | 1500
3F | CSSD | 308, 309, 306, 307, 309, 310, 311 | Sterilization |  | Steam Stelizer | 2 | 36000 | 72000
[5 empty] | Sealing Machine | 2 | 500 | 1000
[5 empty] | U/S Instrument Washer | 1 | 7000 | 7000
[5 empty] | Drying Cabinet | 1 | 7000 | 7000
[5 empty] | Washer/ Disinfector | 1 | 5000 | 5000
[5 empty] | Flash Sterilizer | 1 | 2500 | 2500
[5 empty] | ETO Sterilizer | 1 | 2000 | 2000
3F | OT | 358, 359, 356, 355, 353, 352, 380 | Operation Theatre Services. | 6 | O. T. Table | 6 | 400 | 2400 | 2400
[5 empty] | O.T. Light | 6 | 400 | 2400 | 2400
[5 empty] | Detibrillator | 6 | 70 | 420
[5 empty] | Anaesthesia Station | 6 | 200 | 1200 | 1200
[5 empty] | Monitor | 6 | 120 | 720 | 720
[5 empty] | Electro Cautery | 6 | 800 | 4800 | 4800
[5 empty] | C- Arm | 2 | 7000 | 14000
[5 empty] | Lisasure | 2 | 500 | 1000 | 1000
[5 empty] | Harmonic Scalpel | 2 | 550 | 1100 | 1100
[5 empty] | Argon Cautery | 1 | 500 | 500 | 500
[5 empty] | Endoscopic Set. | 2 | 3000 | 6000 | 6000
[5 empty] | Operating Microscope | 2 | 500 | 1000 | 1000
[5 empty] | Syringe Pump | 18 | 20 | 360
[5 empty] | Flash Sterilizer | 1 | 2500 | 2500
[5 empty] | Body Warmer | 6 | 1200 | 7200
3F | Recovery | 347 | Recovery | 8 Beds. | Monitor | 12 | 120 | 1440 | 1440
[5 empty] | Defibrillator | 1 | 70 | 70
[5 empty] | Pube Oximeter | 2 | 70 | 140
[5 empty] | Syringe Pump | 8 | 20 | 160
[5 empty] | Suction Machine | 2 | 750 | 1500
3F | ICU | 328 | ICU | 8 Beds. | Central Station | 1 | 500 | 500 | 500
[5 empty] | Monitor | 8 | 120 | 960 | 960
[5 empty] | Ventilator | 4 | 500 | 2000 | 2000
[5 empty] | ECG Machine | 1 | 50 | 50
[5 empty] | Pube Oximeter | 2 | 70 | 140
[5 empty] | Syringe Pump | 8 | 20 | 160
[5 empty] | Infusion Pumps | 4 | 20 | 80
[5 empty] | Nebulizer | 2 | 25 | 50
[5 empty] | Suction Machine | 2 | 750 | 1500
[5 empty] | Portable U/S | 1 | 2000 | 2000 | 2000
[5 empty] | Portable X- Ray | 1 | 7000 | 7000
[5 empty] | Body Warmer | 3 | 1200 | 3600
[5 empty] | Total load on generator |  |  | 670550 | 77990