## Sheet1
Table E-9 : Design Considerations : Life Period of Electrical Items as per DMRC
All equipment, cables and wiring shall be designed, manufactured and installed so as to secure a service life as shown below:
· Main switchboards | 30 Years
· Transformers | 30 Years
· Sub-main switchboards | 30 Years
· Cables | 30 Years
· Fire alarm main panel | 30 Years
· Luminaires | 20 Years
· Tray, trunking and supports | 30 Years
· Lightning protection | 30 Years
· Sub-assemblies and components | 30 Years
· All other equipment | minimum 20 Years
Switchboards, equipment, and components shall be rated for operation in ambient temperatures of 50oC and humidity up to 75%.