## duct
Table HVAC 8 : Duct Selection
Table HVAC 8(a) : Duct For Air Velocity
SN | Type of Duct | Comfort systems | Industrial systems | High speed systems
1 | Main ducts | 4 – 7 m/s | 8 – 12 m/s | 10 – 18 m/s
2 | Main branch ducts | 3 – 5 m/s | 5 – 8 m/s | 6 – 12 m/s
3 | Branch ducts | 1 – 3 m/s | 3 – 5 m/s | 5 – 8 m/s
Table 8(b) Equivalent duct sizes for rectangular and circular duct delivering air airflows at different CFM.
SN | CFM (Cubic Feet per Minute) | Equivant Rectangular Duct Sizes (Inches) | Equivant Round Duct Sizes (Inches) | SN | CFM (Cubic Feet per Minute) | Equivant Rectangular Duct Sizes (Inches) | Equivant Round Duct Sizes (Inches)
1 | 100 | 3 X 4 | 4 | 36 |  | 15 X 18
2 | 200 | 3 X 7 | 5 | 37 | 7000 | 12 X 26 | 20
3 |  | 4 X 5 |  | 38 |  | 16 X 20
4 | 300 | 4 X 7 | 6 | 39 | 8000 | 12 X 30 | 21
5 |  | 5 X 6 |  | 40 |  | 14 X 25
6 | 400 | 4 X 9 | 7 | 41 | 9000 | 12 X 34 | 22
7 |  | 5 X 7 |  | 42 |  | 15 X 25
8 |  | 6 X 6 |  | 43 | 10000 | 12 X 36 | 23
9 | 500 | 6 X 7 | 8 | 44 |  | 16 X 25
10 | 750 | 5 X 12 | 9 | 45 |  | 20 X 20
11 |  | 6 X 10 |  | 46 | 12500 | 12 X 45 | 24
12 |  | 7 X 8 |  | 47 |  | 16 X 30
13 | 1000 | 7 X 10 | 10 | 48 |  | 20 X 24
14 |  | 8 X 9 |  | 49 | 15000 | 16 X 36 | 26
15 | 1250 | 8 X 10 | 10 | 50 |  | 18 X 30
16 |  | 9 X 9 |  | 51 |  | 23 X 25
17 | 1500 | 8 X 12 | 12 | 52 | 17500 | 16 X 40 | 28
18 |  | 10 X 10 |  | 53 |  | 20 X 32
19 | 1750 | 8 X 14 | 12 | 54 |  | 25 X 25
20 |  | 9 X 12 |  | 55 | 20000 | 16 X 45 | 30
21 |  | 10 X 11 |  | 56 |  | 20 X 35
22 | 2000 | 8 X 15 | 12 | 57 |  | 25 X 28
23 |  | 10 X 12 |  | 58 | 25000 | 16 X 55 | 32
24 | 2500 | 10 X 14 | 14 | 59 |  | 20 X 43
25 |  | 12 X 12 |  | 60 |  | 25 X 38
26 | 3000 | 12 X 14 | 14 | 61 | 30000 | 20 X 50 | 34
27 | 3500 | 12 X 15 | 15 | 62 |  | 30 X 32
28 | 4000 | 10 X 22 | 16 | 63 | 35000 | 20 X 55 | 36
29 |  | 14 X 15 |  | 64 |  | 30 X 35
30 | 4500 | 12 X 19 | 17 | 65 | 40000 | 25 X 48 | 38
31 |  | 14 X 16 |  | 66 |  | 30 X 40
32 | 5000 | 10 X 25 | 17 | 67 | 45000 | 25 X 25 | 40
33 |  | 12 X 20 |  | 68 |  | 32 X 40
34 |  | 15 X 16 |  | 69 | 50000 | 32 X 45 | 42
35 | 6000 | 14 X 20 | 19 | 70 |  | 35 X 40