## ilu
Table E-4 : Lighting Density as per ECBC 2017
The following are the details taken from ECBC 2007.
7.3 Interior Lighting Power
The installed interior lighting power for a building or a separately metered or permitted
portion of a building shall be calculated in accordance with § 7.3.3 and shall not exceed the
interior lighting power allowance determined in accordance with either § 7.3.1 or § 7.3.2.
Tradeoffs of interior lighting power allowance among portions of the building for which a
different method of calculation has been used are not permitted.
Exception to § 7.3: The following lighting equipment and applications shall not be considered
when determining the interior lighting power allowance, nor shall the wattage for such
lighting be included in the installed interior lighting power. However, any such lighting shall
not be exempt unless it is an addition to general lighting and is controlled by an independent
control device.
(a) Display or accent lighting that is an essential element for the function performed in
galleries, museums, and monuments,
(b) Lighting that is integral to equipment or instrumentation and is installed by its
manufacturer,
(c) Lighting specifically designed for medical or dental procedures and lighting integral to
medical equipment,
(d) Lighting integral to food warming and food preparation equipment,
(e) Lighting for plant growth or maintenance,
(f) Lighting in spaces specifically designed for use by the visually impaired,
(g) Lighting in retail display windows, provided the display area is enclosed by ceilingheight
partitions,
(h) Lighting in interior spaces that have been specifically designated as a registered
interior historic landmark,
(i) Lighting that is an integral part of advertising or directional signage,
(j) Exit signs,
(k) Lighting that is for sale or lighting educational demonstration systems,
(l) Lighting for theatrical purposes, including performance, stage, and film or video
production, and
(m) Athletic playing areas with permanent facilities for television broadcasting.
7.3.1 Building Area Method
Determination of interior lighting power allowance (watts) by the building area method shall
be in accordance with the following:
(a) Determine the allowed lighting power density from Table 7.3.1 for each appropriate
building area type.
(b) Calculate the gross lighted floor area for each building area type.
(c) The interior lighting power allowance is the sum of the products of the gross lighted floor
area of each building area times the allowed lighting power density for that building area
types.
Table 7.3.1 Interior Lighting Power - Building Area Method
Building Area Type | LPD (W/m2) | Building Area Type | LPD (W/m2)
Automotive Facility | 9.7 | Multifamily | 7.5
Convention Center | 12.9 | Museum | 11.8
Court House | 12.9 | Office | 10.8
Dining: Bar Lounge/Leisure | 14
Dining: Cafeteria/Fast Food | 15.1 | Penitentiary | 10.8
Dining: Family | 17.2 | Performing Arts Theater | 17.2
Dormitory | 10.8 | Police/Fire Station | 10.8
Exercise Center | 10.8 | Post Office | 11.8
Gymnasium | 11.8 | Religious Building | 14
Healthcare-Clinic | 10.8 | Retail | 16.1
Hospital/Health Care | 12.9 | School/University | 12.9
Hotel | 10.8 | Sports Arena | 11.8
Library | 14 | Town Hall | 11.8
Manufacturing Facility | 14 | Transportation | 10.8
Motel | 10.8 | Warehouse | 8.6
Motion Picture Theater | 12.9 | Workshop | 15.1
7.3.2 Space Function Method
Determination of interior lighting power allowance (watts) by the space function method shall
be in accordance with the following:
(a) Determine the appropriate building type from Table 7.3.2 and the allowed lighting power
density.
(b) For each space enclosed by partitions 80% or greater than ceiling height, determine the
gross interior floor area by measuring to the center of the partition wall. Include the floor
area of balconies or other projections. Retail spaces do not have to comply with the 80%
partition height requirements.
(c) The interior lighting power allowance is the sum of the lighting power allowances for all
spaces. The lighting power allowance for a space is the product of the gross lighted floor
area of the space times the allowed lighting power density for that space.
Table 7.3.2 Interior Lighting Power – Space Function Method
Space Function | LPD (W/m2) | Space Function | LPD (W/m2)
Office-enclosed | 11.8 | Library
Office-open plan | 11.8 | Card File & Cataloging | 11.8
Conference/Meeting/Multipurpose | 14 | Stacks | 18.3
Classroom/Lecture/Training | 15.1 | Reading Area | 12.9
Lobby | 14 | Hospital
For Hotel | 11.8 | Emergency | 29.1
For Performing Arts Theater | 35.5 | Recovery | 8.6
For Motion Picture Theater | 11.8 | Nurse Station | 10.8
Audience/Seating Area | 9.7 | Exam Treatment | 16.1
For Gymnasium | 4.3 | Pharmacy | 12.9
For Exercise Center | 3.2 | Patient Room | 7.5
For Convention Center | 7.5 | Operating Room | 23.7
For Religious Buildings | 18.3 | Nursery | 6.5
For Sports Arena | 4.3 | Medical Supply | 15.1
For Performing Arts Theater | 28 | Physical Therapy | 9.7
For Motion Picture Theater | 12.9 | Radiology | 4.3
For Transportation | 5.4 | Laundry – Washing | 6.5
Atrium-first three floors | 6.5 | Automotive – Service Repair | 7.5
Atrium-each additional floor | 2.2 | Manufacturing
Lounge/Recreation | 12.9 | Low Bay (<8m ceiling) | 12.9
For Hospital | 8.6 | High Bay (>8m ceiling) | 18.3
Dining Area | 9.7 | Detailed Manufacturing | 22.6
For Hotel | 14 | Equipment Room | 12.9
For Motel | 12.9 | Control Room | 5.4
For Bar Lounge/Leisure Dining | 15.1 | Hotel/Motel Guest Rooms | 11.8
For Family Dining | 22.6 | Dormitory – Living Quarters | 11.8
Food Preparation | 12.9 | Museum
Laboratory | 15.1 | General Exhibition | 10.8
Restrooms | 9.7 | Restoration | 18.3
Dressing/Locker/Fitting Room | 6.5 | Bank Office – Banking Activity Area | 16.1
Corridor/Transition | 5.4 | Religions Buildings
For Hospital | 10.8 | Worship-pulpit, choir | 25.8
For Manufacturing Facility | 5.4 | Fellowship Hall | 9.7
Stairs-active | 6.5 | Retail
Active Storage | 8.6 | Sales Area | 18.3
For Hospital | 9.7 | Mall Concourse | 18.3
Inactive Storage | 3.2 | Sports Arena
For Museum | 8.6 | Ring Sports Area | 29.1
Electrical/Mechanical | 16.1 | Court Sports Area | 24.8
Workshop | 20.5 | Indoor Field Area | 15.1
Sleeping Quarters | 3.2 | Warehouse
Convention Center – Exhibit Space | 14 | Fine Material Storage | 15.1
|  | Medium/Bulky Material Storage | 9.7
Parking Garage – Garage Area | 2.2
Transportation
Airport – Concourse | 6.5
Air/Train/Bus – Baggage Area | 10.8
Terminal – Ticket Counter | 16
7.3.3 Installed Interior Lighting Power
The installed interior lighting power calculated for compliance with § 7.3 shall include all
power used by the luminaires, including lamps, ballasts, current regulators, and control
devices except as specifically exempted in § 7.1.
Exception to § 7.3.3: If two or more independently operating lighting systems in a space are
controlled to prevent simultaneous user operation, the installed interior lighting power shall
be based solely on the lighting system with the highest power.
7.3.3.1 Luminaire Wattage
Luminaire wattage incorporated into the installed interior lighting power shall be determined
in accordance with the following:
(a) The wattage of incandescent luminaires with medium base sockets and not
containing permanently installed ballasts shall be the maximum labeled wattage of
the luminaires.
(b) The wattage of luminaires containing permanently installed ballasts shall be the
operating input wattage of the specified lamp/ballast combination based on values
from manufacturers’ catalogs or values from independent testing laboratory reports.
(c) The wattage of all other miscellaneous luminaire types not described in (a) or (b)
shall be the specified wattage of the luminaires.
(d) The wattage of lighting track, plug-in busway, and flexible-lighting systems that allow
the addition and/or relocation of luminaires without altering the wiring of the system
shall be the larger of the specified wattage of the luminaires included in the system
or 135 W/m (45 W/ft). Systems with integral overload protection, such as fuses or
circuit breakers, shall be rated at 100% of the maximum rated load of the limiting
device.
7.4 Exterior Lighting Power
For building exterior lighting applications specified in Table 7.4, the connected lighting power
shall not exceed the specified lighting power limits specified for each of these applications.
Trade-offs between applications are not permitted. Exterior lighting for all other applications
(except those included in the Exceptions to § 7.4) shall comply with the requirements of §
7.2.3.
Table 7.4 Exterior Building Lighting Power
Exterior Lighting Applications Power Limits
Building entrance (with canopy) 13 W/m2 (1.3 W/ft2) of canopied area
Building entrance (without canopy) 90 W/lin m (30 W/lin f) of door width
Building exit 60 W/lin m (20 W/lin f) of door width
Building facades 2 W/m2 (0.2 W/ft2) of vertical facade area
Exceptions to § 7.4: Lighting used for the following exterior applications is exempt when
equipped with an independent control device:
(a) Specialized signal, directional, and marker lighting associated with transportation;
(b) Lighting used to highlight features of public monuments and registered historic
landmark structures or buildings;
(c) Lighting that is integral to advertising signage; or
(d) Lighting that is specifically designated as required by a health or life safety statute,
ordinance, or regulation.
General Recommendation Trade Practice
Type of Building/Room | Light Power | Type of Building/Room | Light Power
| (Watts/Sq.Ft.) |  | (Watts/Sq.Ft.)
Apartments | 1.0 - 4.0 | Luncheonettes | 1.5 - 2.5
Banks | 2.0 - 5.0 | Lunch Rooms | 1.5 - 2.5
Bars | 1.5 - 2.0 | Malls | 1.0 - 3.0
Cafeterias | 1.5 - 2.5 | Medical Centers | 1.5 - 2.5
Churches | 1.0 - 3.0 | Motels Public Areas | 1.5 - 3.0
Clubhouses | 1.5 - 2.0 | Motels Guest Rooms | 1.0 - 3.0
Cocktail Lounges | 1.5 - 2.0 | Municipal Buildings | 2.0 - 5.0
Computer Rooms | 1.5 - 5.0 | Museums | 1.0 - 3.0
Court Houses | 2.0 - 5.0 | Nightclubs | 1.5 - 2.0
Dental Centers | 1.5 - 2.5 | Nursing Home Patient Rooms | 2.0 - 3.0
Department Stores | 1.0 - 3.0 | Police Stations | 2.0 - 3.0
Dining Halls | 1.5 - 2.5 | Post Offices | 2.0 - 3.0
Drug Store | 1.0 - 3.0 | Precision Manufacturing | 2.0 - 3.0
Fire Stations | 2.0 - 3.0 | Residential | 1.0 - 4.0
Hospitals, General Areas | 1.5 - 2.5 | Retail Stores | 2.0 - 6.0
Hotels Public Spaces | 1.5 - 3.0 | Restaurants | 1.5 - 3.0
Kindergarten | 1.0 - 3.0 | School Classrooms | 2.0 - 6.0
Kitchens | 1.5 - 3.0 | Shops | 1.0 - 3.0
Jail | 1.0 - 2.5 | Supermarkets | 1.0 - 3.0
Libraries | 1.0 - 3.0 | Taverns | 1.5 - 2.0
|  | Town Halls | 2.0 - 5.0