## infiltration
Table 10.9 Infilteration through doors based on usage (wind velocity 12 kmph.)
Application | cmm/ Person in Rooms Door
| 180 cm (6') | 90 cm (3') swinging Door.
| Revolving Door | No vestibule or ante room | With Vestibule or antiroom
Bank | 0.184 | 0.227 | 0.17
Barber Shop | 0.113 | 0.142 | 0.108
Soda Shop | 0.156 | 0.198 | 0.15
Cigar Store | 0.566 | 0.85 | 0.637
Departmental Store | 0.182 | 0.227 | 0.17
Dress shop | 0.057 | 0.071 | 0.108
Drug store | 0.156 | 0.198 | 0.15
Hospital | - | 0.099 | 0.637
Lunch Room | 0.113 | 0.142 | 0.17
Men's shop | 0.076 | 0.105 | 0.054
Restaurant | 0.057 | 0.071 | 0.15
Shoe Store | 0.076 | 0.0099 | 0.074
Table 10. 10 Infilteration through doors on adjacent walls (12 kmph).
Description |  | cmm per sq.m. of door area
Normally open
|  | Normally close | Average use | No. Vestibule | With Vestibule
1 | Revolving doors normal operation. | 0.24 | 1.58 | - | -
2 | Revolving doors with panels open. | - | - | 34 | 25
3 | Glass doors 4.75 mm crack | 1.37 | 3 | 20 | 14
4 | Wood door | 0.3 | 1.98 | 20 | 14
5 | Garage's doors. | 0.61 | 1.37 | - | -
6 | Small factory doors. | 0.23 | 1.98 | - | -
Table 10.11 . Infiltration Through Swinging Doors on Opposite walls
(Wind velocity 12 Kmph).
% Time 2nd Door is open | Cmm/ Pair of Doors
% Time 1st Door is open.
| 10 | 25 | 50 | 75 | 100
10 | 2.8 | 7 | 14 | 21 | 28
25 | 7.1 | 18 | 35 | 53 | 71
50 | 14 | 35 | 71 | 106 | 142
75 | 21 | 53 | 106 | 159 | 210
100 | 28 | 71 | 142 | 210 | 280
Table HVAC - 12 : Infiltration through Doors- Crack Method
Type of Door | Cmm per metre of Crack | Wind Velocity, Kmph
|  | 8 | 16 | 24 | 32 | 40 | 48
Glass door
(a) | Good Installation 3.2 mm crack | 0.3 | 0.6 | 0.9 | 1.21 | 1.49 | 1.77
(b) | Average installation 4.76 mm crack | 0.45 | 0.96 | 1.3 | 1.86 | 2.23 | 2.7
(c ) | Poor installation 6-4 mm crack | 0.6 | 1.21 | 1.77 | 2.42 | 2.42 | 3.53
Ordinary wood or metal door.
(a) | Well fitted W- stripped | 0.04 | 0.06 | 0.08 | 0.12 | 0.16 | 0.2
(b) | Well fitted not W- stripped. | 0.08 | 0.11 | 0.17 | 0.24 | 0.31 | 0.39
(c ) | Poorly fitted not W- stripped | 0.08 | 0.21 | 0.34 | 0.48 | 0.61 | 0.78
(d) | Factory door 3.2 mm crack | 0.3 | 0.6 | 0.9 | 1.21 | 1.49 | 1.77
l