## heatgain
Table HVAC-13 : Approximate Heat Gain from Occupants in Air Conditioned Spaces.
The table below can be used to estimate the sensible and latent heat from people. The values can be used to calculate the heat load handled by the air condition system.
Degree of Activity | Typical Application | Average Metabolic rate - male adult (W) | Room Dry Bulb Temperature (oC)
|  |  | 28 |  | 27 |  | 26 |  | 24 |  | 22 |  | 20
|  |  | Sens. | Lat. | Sens. | Lat. | Sens. | Lat. | Sens. | Lat. | Sens. | Lat. | Sens. | Lat.
Seated at rest | Cinema, theatre, school | 100 | 50 | 50 | 55 | 45 | 60 | 40 | 67 | 33 | 72 | 28 | 79 | 21
Seated, very light work | Gomputer working | 120 | 50 | 70 | 55 | 65 | 60 | 60 | 70 | 50 | 478 | 42 | 84 | 36
Office work | Hotel reception, cashier | 130 | 50 | 80 | 56 | 74 | 60 | 70 | 70 | 60 | 78 | 52 | 86 | 44
Standing, walking slowly | Laboratory work | 130 | 50 | 80 | 56 | 74 | 60 | 70 | 70 | 60 | 78 | 52 | 86 | 44
Walking, seated |  | 150 | 53 | 97 | 58 | 92 | 64 | 86 | 76 | 74 | 84 | 66 | 90 | 60
Moderate work | Servant, hair dresser | 160 | 55 | 105 | 60 | 100 | 68 | 92 | 80 | 80 | 90 | 70 | 98 | 62
Light bench work | Mechanical production | 220 | 55 | 165 | 52 | 158 | 70 | 150 | 85 | 135 | 100 | 120 | 115 | 105
Moderate Dancing | Party | 250 | 62 | 188 | 70 | 180 | 78 | 172 | 94 | 156 | 110 | 140 | 125 | 125
Fast walking | Mountain walking | 300 | 80 | 220 | 88 | 212 | 96 | 204 | 110 | 190 | 130 | 170 | 145 | 155
Heavy work | Athletics | 430 | 132 | 298 | 138 | 292 | 144 | 286 | 154 | 276 | 170 | 260 | 188 | 242
Typical Application | Sensible Heat | Latent Heat
| (btu/hr) | (btu/hr)
Theater-Matinee | 200 | 130
Theater-Evening | 215 | 135
Offices, Hotels, Apartments | 215 | 185
Retail & Department Stores | 220 | 230
Drug Store | 220 | 280
Bank | 220 | 280
Restaurant | 240 | 310
Factory | 240 | 510
Dance Hall | 270 | 580
Factory | 330 | 670
Bowling Alley | 510 | 940
Factory | 510 | 940
Tabulated values are based on 78oF for dry-bulb temperature.
Adjusted total heat value for sedentary work, restaurant, includes 60 Btu/hr for food per individual (30 Btu/h sensible and 30 Btu/ latent heat).
For bowling figure one person per alley actually bowling, and all others as sitting (400 Btu/h) or standing (550 Btu/h).