## ref
Table HVAC-14 : Properties of Refrigerants
SN | Refrigerant | Formula | Boiling Temp. | Critical Temp. | Properties | Applications
|  |  | oC | oC
| Ammonia | NH3 | -33 | 133 | Penetrating odour, soluble in water. harmless in concentration up to 1/30%, non flammable, explosive | Large industrial plants
| R12 | C Cl2F2 | -29,8 | 112 | Little odour, colourlessas gass or liquid, non flammable, non corrosive of ordinary metals, stable | Small plants with reciprocating compressors.
| R11 | C Cl3F | 8,9 | 198 | Non flammable, non corrosive non toxic, stable | Commercial plants with centrifugal compressors.
| R22 | CH Cl F2 | -40,8 | 96 | Little odour, colourless as gas or liquid, non toxic, non irritating, non flammable, non corrosive, stable | Packaged airconditioning units where size of equipment and economy are important.
| R500 | C Cl2 F2 (73,8%) | -33 |  | Simmilar to R12 | Offers aprox. 20% more refrigeration capacity than R12 for same compressor.
CH3 CH F2 (26.2%)
| R502 | C Cl F2 (48,8%) + F2 - CF3 (51.2%) | -45,6 | 90,1 | Non flammable, non toxic, non corrosive, stable | Capacity comparable to R22.
| R134a | Tetrafluoroethane (CF3CH2F) | -26.1°C. |  | It is safe for normal handling as it is non-toxic, non-flammable and non-corrosive. | Used as a replacement for R-12 CFC refrigerant in the area of centrifugal, rotary screw, scroll andreciprocating compresssors.
Properties of R-134a
|  |  |  | No | Properties | R-134a
|  |  |  | 1 | Boiling Point | -14.9°F or -26.1°C
|  |  |  | 2 | Auto-Ignition Temperature | 1418°F or 770°C
|  |  |  | 3 | Ozone Depletion Level | 0
|  |  |  | 4 | Solubility In Water | 0.11% by weight at 77°F or 25°C
|  |  |  | 5 | Critical Temperature | 252°F or 122°C
|  |  |  | 6 | Cylinder Color Code | Light Blue
|  |  |  | 7 | Global Warming Potential (GWP) | 1200
Latest Development
The recent discovery that R-134a contributes to global warming has caused the European Union to ban its use on new carsstarting from year 2011. Other countries are expected to follow suit.
Refrigerants related to HFCs group
R 125 refrigerant. Chemical formula СНF2СF3
Related to HFC group, it does not contain chlorine. Ozone depletion potential ODP = 0, global warming potential GWP = 860. Boiling point at the atmospheric pressure is -48,1 oС. The refrigerant is reccomended to use in a clear type or as a component of alternative blends to substitute R22, R502 and R12. R125 refrigerant is fire safe. As to energy performance and heat-transfer coefficient, it plays back to R22 and R502 refrigerants. Compared to R502, it has more abrupt curve characterizing dependence of saturated vapors pressure on temperature, low critical temperature and not high specific temperature of heat-vapor buildup which causes the necessity of increase of the compression level. In connection with this, possibilities of R125 use in the refrigeration equipment using condensers with air cooling are extremely limited.
At the same time, R125 has lower (compared to R22 and R502) discharge temperature and high mass flow under low suction pressures. Piston refrigeration compressors operating on R125 are characterized by optimal cylinder charging, and as a consequence, they have big volume efficiency.
R134a refrigerant. Chemical formula CF3CFH2 (tetrafluoroethane).
R134a molecule has smaller size than R12 molecule which makes danger of leakage more considerable. Related to HFC group. Ozone depletion potential ODP = 0, global warming potential GWP = 1300.
R134a refrigerant is non-toxic and does not flare up within the whole range of operational temperatures. However, in case of air ingress into the system and compression there can be formed combustible blends. You shouldn't mix R134a with R12 because there is formed azeotrope blend of high pressure with mass proportions of the components 50 and 50%. Saturated vapor pressure of this refrigerant is a bit higher than that of R12 (correspondingly 1,16 and 1,08 МPа at 45 oС). R134a vapor is decomposed under the influence of flame with formation of poisonous and irritating contextures, such as fluorohydrogen.
According to classification ASHRAE, this product is related to class А1. In middle-temperature equipment (boiling point -7 oС and higher), R134a has operation performance close to R12.
R134a is characterized by not high discharge temperature (it is approximately 8...10oС lower than for R12) and not high values of saturated vapors pressure.
In refrigeration facilities operating under boiling point lower than -15 oС, energy data of R134a are worse than those of R12 ( specific volumetric refrigerating effect is 6% lower at -18 oС), and refrigerating factor. In such facilities it is purposeful to use refrigerants with lower normal boiling point or compressor with increased time volume circumscribed by pistons.
In middle temperature refrigeration facilities and air-conditioning systems, refrigerating factor of R134a is equal to the factor for R12 or higher than that.
In high-temperature refrigeration facilities, specific cold-productivity when operating on R134a is also a bit higher (6% more at tо = t0 oС), than that of R12. Ranges of using R134a refrigerant are shown in Fig., and dependence of cold-productivity and refrigerating factor on boiling point is shown further on the figure.
Due to considerable global warming potential GWP, it is recommended to use R134a in hermetic refrigerating systems. Contribution of R134a to greenhouse effect is 1300 times as bigger as that of СО2. Thus, air venting of R134a one filling from a domestic refrigerator (about 140 gm) corresponds to ejection of 170 kg of СО2. In Europe about 448 gm of СО2 is formed at production of 1 kWt/h of power, that is, this ejection corresponds to production of 350 kWt*h of power.
For operation with R134a refrigerant, only polyester refrigeration oils characterized by increased hygroscopic property are recommended.
R134a is widely used all over the world as a main substitute of R12 fir refrigeration equipment operating within middle-temperature range. It is used in automobile air-conditioners, domestic refrigerators, commercial refrigeration middle-temperature equipment, industrial facilities, air-conditioning systems in buildings and industrial areas, as well as on refrigeration transport. The refrigerant can be used also for retrophite of the equipment operating at lower temperatures. However, in this case, if the compressor is not substituted, refrigeration system can have reduced cold-productivity.
R134a is compatible with a number of sealing materials, in particular, with pads made of such materials as "Buna-N", "Khailalon 48", "Neopren", "Nordel". As the analysis carried out by company "Du Pont" showed, change of mass and linear swelling of such materials used in domestic refrigeration equipment as phenoplast and polyamide chocks, textolite, paronite and polyethylene terephtalate skins, in combination of SUVA R134a with polyester oil "Castrol SW100" at 100 oС during 2 weeks have been insignificant.
R134a is compatible with a number of sealing materials, in particular, with pads made of such materials as "Buna-N", "Khailalon 48", "Neopren", "Nordel". As the analysis carried out by company "Du Pont" showed, change of mass and linear swelling of such materials used in domestic refrigeration equipment as phenoplast and polyamide chocks, textolite, paronite and polyethylene terephtalate skins, in combination of SUVA R134a with polyester oil "Castrol SW100" at 100 oС during 2 weeks have been insignificant.
Analysis of foreign publications and the results of the research of native specialists indicate that substitution of R12 for R134a, which has high global warming potential GWP, in refrigeration compressors is connected with solution of a number of technical tasks basic of which are:
Improvement of volume and energy performance of hermetic compressors;
Increasing of chemical constancy of enamel wires of the hermetic compressor electric motor;
Increasing of dehumidifying ability of filter-dehydrators due to high hygroscopic property of R134a system - synthetic oil.
All this should result in considerable increase of the cost of refrigeration equipment. At the same time, in water-cooling plants with screw and centrifugal compressors the use of R134a has certain perspectives.
R 143a refrigerant. Chemical formula CF3-СН3 (trifluoroethane)
R143a has ozone depletion potential ODP = 0 and comparatively high global warming potential GWP = 1000, non-toxic and fire-safe, it does not interact with structural and packing materials. Three hydrogen atoms in R143a molecule contribute to good solubility in mineral oils. Specific heat of vaporization is 19,88 kJoule/mole at normal boiling point which is a bit higher than for R125 (18,82 kJoule/mole). Discharge temperature is lower than that of R12, R22 and R502. As energy analysis has showed, energy effectiveness of two-step cycle with R143a is close to the effectiveness of the cycle with R502, lower than that of R22, and higher than that of R125. R143a refrigerant belongs to composition of multi-component alternative blends suggested for substitution of R12, R22 and R502.
R 32 refrigerant. Chemical formula CF2H2 (difluoromethane).
Related to HFC group. R32 has ozone depletion potential ODP = О and low global warming potential GWP = 220, in comparison with R125 and R143a. Non-toxic, fire risky. It has high specific heat of vaporization 20,37 kJoule/mole at normal boiling point and abrupt dependence of saturated vapors pressure on the temperature and, as a result, R32 is characterized by high discharge temperature, which is the highest of all alternative refrigerants, except ammonia. R32 is soluble in polyester oils.
When used in refrigeration facilities, R32 is characterized by high cold-productivity and energy effectiveness, but it is slightly inferior to R22 and R717. High level of R32 compression causes necessity of considerable alteration in the refrigeration facility design at retrophite, and as a consequence, it results in increasing of its metal intensity and cost. Therefore, R32 is recommended to use mainly as a component of alternative working blend. Due to small size of R32 molecule compared to molecules of ethane row refrigerants, R32 selective leakage through looseness in the refrigerating system is possible, which can change the composition of multi-component working blend.