## exhaust
Table HVAC-16 : Minimum Exhaust Air Requirements/Room Pressure
SN | Areas | Room Pressure | Exhaust Air Air Changes/Hr
| Admitting and Waiting Areas | Negative | SA + 15 Percent of SA
| Ambulance Entrance | Negative | 10
| Animal Research | Negative | SA + 15 Percent of SA
| Ante Rooms | See Standard Detail 15900-7 or 15900-7A
| Autopsy Suite (All Rooms) | Negative | SA + 15 Percent of SA
| Battery Charging Areas | Negative | 8
| Bathing Facilities | Negative | 10
| Bathrooms | Negative | 10
| BMT Patient Areas | Positive | SA – 15 Percent of SA
| Ceramics Rooms (dental Prosthetics Laboratories) | Positive | SA – 15 Percent of SA
| Clean and Preparation Rooms (SPD Suites) | Positive | SA – 15 Percent of SA
| Clean Rooms (Laundry Facilities) | Positive | SA – 15 Percent of SA
| Dark Rooms | Negative | SA + 15 Percent of SA
| Detergent Storage | Negative | SA + 15 Percent of SA
| Dialysis | Positive | SA – 15 Percent OF SA
| Dietetics {See Note (a)} | Negative | SA + 15 Percent of SA
| Enema or Hopper Rooms | Negative | 15
| Examination Rooms (MRI Suites) | Equal | 12
| Flammable Storage | Negative | 0.3 Cu M/Min/0.1 Sq M, 4.2 Cu M/Min Minimum (1.0 CFM/Sq Ft, 150 CFM Minimum)
| Gas Storage | Negative | 0.3 Cu M/Min/0.1 Sq M, 4.2 Cu M/Min Minimum (1.0 CFM/Sq Ft, 150 CFM Minimum)
| Glass and Cage Washing Areas | Negative | See Notes
| Instrument Rooms (Sterile) | Positive | SA – 15 Percent of SA
| Intensive Care Units (ICUs) | Positive | SA – 15 Percent of SA See Article 3.10
| Isolation Rooms (Negative Pressure) | See VA STD Detail 15900-7 | SA + 15 Percent of SA
(All Articles listed in Table 3-5 and Table 3-6) and paragraph 2.11.6
| Isolation Rooms (Positive Pressure) | See VA STD Detail 15900-7A
| Aids Patient Rooms | Positive | SA – 15 Percent of SA
| Burn Units | Positive | SA – 15 Percent of SA
| Leukemia Patient Rooms | Positive | SA – 15 Percent of SA
| Organ Transplant Rooms | Positive | SA – 15 Percent of SA
| Janitor Closet (HAC) | Negative | 10
| Kitchen (See Note b) | Negative | SA + 15 Percent of SA
| Laboratories | Negative | SA + 15 Percent of SA See Article 3.13
| Laundry (Central Facility) | Negative | See Article 3.14
| Locker Rooms {See Note (c)} | Negative | SA + 15 Percent
See Note (c)
Medical Media Service (MMS) See Article 3.16
| Minor Operating Rooms (O.R.s) (Trauma Rooms) | Positive | See Article 3.1.2
| Operating Rooms (Surgery Suites) | Positive | See Article 3.21
| Oral Surgery and Treatment | Positive | SA – 15 Percent of SA
| Radiation Therapy | Negative | SA + 15 Percent of SA
| Reagent Grade Water Treatment Rooms | Negative | 8
| Recovery Rooms | Positive | SA – 15 Percent of SA
| Silver Recovery Rooms | Negative | 6
| Smoking Area | Negative | 12
| Soiled Dishwashing Rooms | Negative | 6
| Soiled Linen Rooms | Negative | 6
| Soiled Utility Rooms | Negative | 6
Special Procedure Rooms
| Bronchoscopy | Negative | SA + 15 Percent of SA
| Cardiac Catheterization | Positive | SA – 15 Percent of SA
| Colonoscopy/EGD | Negative | SA + 15 Percent of SA
| Cystoscopy | Positive | SA – 15 Percent of SA
| Endoscopy | Negative | SA + 15 Percent of SA
| Fluoroscopy | Negative | SA + 15 Percent of SA
| GI (Gastrointestinal) | Negative | SA + 15 Percent of SA
| Proctoscopy | Negative | SA + 15 Percent of SA
| Sigmoidoscopy | Negative | SA + 15 Percent of SA
Sterile Corridors (Surgery Suites) See Article 3.21
| Storage Rooms (Soiled or Dirty) | Negative | SA + 15 Percent of SA
| Tissue Culture Rooms | Positive | SA – 15 Percent of SA
| Toilets | Negative | 10
| Treatment Room (Bronchoscopy) | Negative | SA + 15 Percent of SA
| Trash Collection Areas | Negative | 10
| Vestibules | Positive | SA – 15 Percent of SA
| Waiting Rooms | Negative | SA + 15 Percent of SA