## indoor
Table 1-1 Indoor Design Conditions
Recoomendations as per dept of Veterans Washington
| Summer |  |  | Winter
| Db Degrees C (Degrees F) |  | RH Percent | Db Degrees C (Degrees F) | RH Percent
Animal Research (Animal Rooms) | 18 (65) |  | 60 (+5) | 29 (85) | 30 (+5)
Auditoriums | 24 (76) |  | 60 | 22 (72) | --
AIDS Patient Areas | 24 (76) |  | 50 | 25 (78) | 30
Autopsy Suites | 24 (76) |  | 60 | 24 (76) | 30
Bathrooms & Toilet Rooms | 25 (78) |  | -- | 22 (72) | --
Blood Banks | 22 (72) |  | 50 | 22 (72) | 30
BMT (Bone Marrow Transplant) Patient Areas | 24 (76) |  | 50 | 25 (78) | 30
Computer Rooms | 21 (70) |  | 40 (+5) | 21 (70) | 40 (+5)
CT Scanner | 24 (76) |  | 50 | 25 (78) | 30
Dialysis Rooms | 25 (78) |  | 50 | 22 (72) | 30
Dining Rooms | 25 (78) |  | 50 | 22 (72) | 30
Dry Labs | 25 (78) |  | 50 | 22 (72) | 30
Electrical Equipment Rooms | Ventilation Only |  |  | 10 (50) | --
Elevator Machine Rooms, Electric Drive | 36 (94) |  | -- | 10 (50) | --
Elevator Machine Rooms, Hydraulic | 36 (94) |  | -- | 10 (50) | --
Emergency Generator | 42 (110) |  | -- | 4 (40) | --
Examination Rooms | 24 (76) |  | 50 | 25 (78) | 30
Gymnasiums | Ventilation Only |  |  | 21 (70) | --
ICUs (Coronary, Medical, Surgical) | 23–29 (75–85) |  | 30–60 | 23–29 (75–85) | 30-60
Isolation Suites | 24 (76) |  | 50 | 25 (78) | 30
Kitchens | 27 (82) |  | 60 | 21 (70) | --
Laboratories | 24 (76) |  | 50 | 22 (72) | 30
Laundries | 28 (84) |  | 60 | 19 (68) | -
Linear Accelerators | 24 (76) |  | 50 | 25 (78) | 30
Locker Rooms | 25 (78) |  | 50 | 22 (72) | 30
Lounges | 25 (78) |  | 50 | 22 (72) | 30
Mechanical Equipment Rooms (MERs) | Ventilation Only |  |  | 10 (50) | --
Medical Media: See Article 3.16
Minor O.R.s (Trauma Rooms) |  | 24 (76) | 50 | 25 (78) | 30
Motor Vehicle Maintenance/Storage |  | Ventilation Only |  | 21 (70) | --
MRI Units |  | 24 (76) | 50 | 25 (78) | 30
Offices, Conference Rooms |  | 25 (78) | 50 | 22 (72) | 30
Operating Rooms (O.R.s) |  | 17–27 (62-80) | 45-55 | 17-27 (62-80) | 45-55
Operating Rooms (O.R.s) - Animal |  | 22 (73) | 50 | 22 (73) | 50
Patient Rooms |  | 24 (76) | 50 | 25 (78) | 30
Pharmacy |  | 22 (72) | 50 | 22 (72) | 30
Radiation Therapy |  | 24 (76) | 50 | 25 (78) | 30
Recovery Units |  | 23 (75) | 50 | 23 (75) | 30
Smoking Area |  | 25 (78) | 50 | 22 (72) | 30
SPECIAL PROCEDURE ROOMS*
Bronchoscopy | 24 (76) |  | 50 | 25 (78) | 30
Cardiac Catheterization | 17–27 (62-80) |  | 45-55 | 17-27 (62-80) | 45-55
Colonoscopy/EGD | 24 (76) |  | 50 | 25 (78) | 30
Cystoscopy | 22 (72) |  | 50 | 25 (78) | 50
Endoscopy | 24 (76) |  | 50 | 25 (78) | 30
Fluoroscopy | 24 (76) |  | 50 | 25 (78) | 30
GI (Gastrointestinal) | 24 (76) |  | 50 | 25 (78) | 30
Proctoscopy | 24 (76) |  | 50 | 25 (78) | 30
Sigmoidoscopy | 24 (76) |  | 50 | 25 (78) | 30
Spinal Cord Injury Units (SCIUs) | 22 (72) |  | 50 | 27 (82) | 30
Supply Processing Distribution (SPD) | 24 (76) |  | 50 | 22 (72) | 30
Ethylene Oxide (ETO) MERs | Ventilation only
Steam Sterilizer MERs | Ventilation only
Telephone Equipment Rooms | 19(65)-23(75) |  | 40-60 | 19(65)-23(75) | 40-60
Therapeutic Pools | 26(80)-29(85) |  | -- | 29 (85) | --
Transformer Rooms | 39 (104) |  | (Maximum)
Treatment Rooms | 24 (76) |  | 50 | 25 (78) | 30
Warehouses | Ventilation Only |  |  | 15 (60) | --
Table 1 : Temperature and humidity requirements in hospitals
Standards | ASHRAE | HTM | Singapore | ASHRAE | HTM | Singapore
Room | Temperature (°C) |  |  | Relative Humidity (%RH)
Operating Theatres | 17~27 | 15~25 | 19- 21 | 45~55 | 40~60 | 50~60
Intensive Care Unit | 24~27 | - | 22-23 | 30~60 | - | 55~65
Wards (airconditioned) | 24 | - | 22~23 | 30~60 | - | 55~65
Isolation Ward | 24~27 | - | 22~23 | 30~60 | - | 55~65
Industry | Process | Temperature oC min | Temperature oC max | Temperature oF min | Temperature oF max | Relative humidity %
Abrasives | Manufacturing | 26 | 26 | 79 | 79 | 50
Ammunition |  | 21 | 21 | 70 | 70 | 40
Bakery | Flour storage | 16 | 26 | 61 | 79 | 55-65
| Production | 23 | 26 | 73 | 79 | 40-70
Billiard Room |  | 23 | 24 | 73 | 75 | 40-50
Bowling Center | Bowling alleys | 23 | 24 | 73 | 75 | 50- 55
| Billiard rooms | 23 | 24 | 73 | 75
Bread | Flour and powdered storage | 21 | 27 | 70 | 80 | 60
| Fermentation | 27 | 27 | 80 | 80 | 75
| Retarding of Dough | 0 | 4 | 32 | 40 | 85
| Final Proof | 35 | 49 | 95 | 120 | 85-90
| Counter flow Cooling | 24 | 24 | 75 | 75 | 80-85
Brewing | Hop storage | -2 | 0 | 29 | 32 | 50-60
| Yeast culture room |  |  |  |  | 80
Candy | Chocolate Pan supply air | 13 | 17 | 55 | 62 | 55-45
| Enrobed room | 27 | 29 | 80 | 85 | 30-25
| Chocolate Cooling Tunnel supply air | 4 | 7 | 40 | 45 | 85-70
| Hand Dippers | 17 | 17 | 62 | 62 | 45
| Molded goods cooling | 4 | 7 | 40 | 45 | 85-70
| Chocolate Packing room | 18 | 18 | 65 | 65 | 50
| Chocolate finished stock storage | 18 | 18 | 65 | 65 | 50
| Centers tempering room | 24 | 27 | 75 | 80 | 35-30
| Marshmallow setting room | 24 | 26 | 75 | 78 | 45-40
| Grained marshmallows drying | 43 | 43 | 110 | 110 | 40
| Gum drying | 52 | 66 | 125 | 150 | 25-15
| Sanded Gum drying | 38 | 38 | 100 | 100 | 25-40
| Gum finished stock storage | 10 | 18 | 50 | 65 | 65
| Sugar pan supply air | 29 | 41 | 85 | 105 | 30-20
| Polishing pan supply air | 21 | 27 | 70 | 80 | 50-40
| Pan rooms | 24 | 27 | 75 | 80 | 35-30
| Nonpareil Pan supply air | 38 | 49 | 100 | 120 | 20
| Hard candy cooling tunnel air | 16 | 21 | 60 | 70 | 55-40
| Hard candy packing | 21 | 24 | 70 | 75 | 40-35
| Hard candy storage | 10 | 21 | 50 | 70 | 40
| Caramel rooms | 21 | 27 | 70 | 80 | 40
Ceramics | Refractory | 43 | 66 | 110 | 150 | 50-90
| Molding room | 27 | 27 | 80 | 80 | 60-70
| Clay storage | 16 | 27 | 60 | 80 | 35-65
| Decalcomania production | 24 | 27 | 75 | 80 | 50
| Decoration room | 24 | 27 | 75 | 80 | 50
Cereal | Packaging | 24 | 27 | 75 | 80 | 45-50
Cheese Curing | Cheddar | 7 | 13 | 45 | 55 | 85-90
| Swiss | 16 | 16 | 60 | 60 | 80-85
| Blue | 9 | 10 | 48 | 50 | 95
| Brick | 16 | 18 | 60 | 65 | 90
| Limburger | 16 | 18 | 60 | 65 | 95
| Camembert | 12 | 15 | 53 | 59 | 90
Clean rooms |  | 21 | 27 | 70 | 80 | 40-60
Distilling | Grain Storage | 16 | 16 | 60 | 60 | 35-40
| General Manufacturing | 16 | 24 | 60 | 75 | 45-60
| Aging | 18 | 22 | 65 | 72 | 50-60
Fruit Storage | Apples | -1 | 4 | 30 | 40 | 90
| Apricots | -1 | 0 | 31 | 32 | 90-95
| Grapefruits (California) | 14 | 16 | 58 | 60 | 85-90
| Grapefruits (Florida) | 10 | 10 | 50 | 50 | 85-90
| Grapes (Eastern) | -1 | 0 | 31 | 32 | 85
| Grapes (Western) | -1 | -1 | 30 | 31 | 90-95
| Lemons | 14 | 16 | 58 | 60 | 86-88
| Oranges (California) | 4 | 7 | 40 | 44 | 85-90
| Oranges (Florida) | 0 | 1 | 32 | 34 | 85-90
| Peaches and Nectarines | -1 | -1 | 31 | 31 | 90
| Plums | -1 | 0 | 30 | 32 | 90-95
| Citrus fruits | 3 | 4 | 38 | 40 | 90-95
Fur | Storage | -2 | 4 | 28 | 39 | 25-40
| Drying | 43 | 43 | 109 | 109
Gum | Manufacturing | 25 | 25 | 77 | 77 | 33
| Rolling | 20 | 20 | 68 | 68 | 63
| Stripping | 22 | 22 | 72 | 72 | 53
| Breaking | 23 | 23 | 74 | 74 | 47
| Wrapping | 23 | 23 | 74 | 74 | 58
Hospitals | Operating, Cystoscopic and fracture rooms | 20 | 24 | 68 | 76 | 50
| Patient rooms | 24 | 24 | 75 | 75 | 40-50
| Intensive care unit | 24 | 24 | 75 | 75 | 40
| Administrative and service areas | 21 | 27 | 70 | 80 | 30-50
Leather | Drying | 21 | 49 | 70 | 120 | 75
| Storage, winter room temperature | 10 | 16 | 50 | 60 | 40-60
Lenses (optical) | Fusing | 24 | 24 | 75 | 75 | 45
| Grinding | 27 | 27 | 80 | 80 | 80
Libraries and Museums | Normal reading and viewing rooms | 21 | 23 | 70 | 74 | 40-50
| Rare manuscript and Storage Vaults | 21 | 22 | 70 | 72 | 45
| Art Storage Areas | 18 | 22 | 65 | 72 | 50
Matches | Manufacture | 22 | 23 | 72 | 74 | 50
| Drying | 21 | 24 | 70 | 75 | 60
| Storage | 16 | 17 | 60 | 62 | 50-55
Meat and fish | Beef (fresh) | 0 | 1 | 32 | 34 | 88-92
| Beef (frozen) | -23 | -18 | -10 |  | 90-95
| Fish (fresh) | 1 | 2 | 33 | 35 | 90-95
| Fish (Frozen) | -23 | -18 | -10 |  | 90-95
| Lamb and Pork (Fresh) | 0 | 1 | 32 | 34 | 85-90
| Lamb and Pork (Frozen) | -23 | -18 | -10 |  | 90-95
Mushrooms | Sweating out period | 49 | 60 | 120 | 140
| Spawn added | 16 | 24 | 60 | 75 | 100
| Growing period | 9 | 16 | 48 | 60 | 80
| Storage | 0 | 2 | 32 | 35 | 80-85
Paint Applications | Oil paint spraying | 16 | 32 | 60 | 90 | 80
| Drying oil paints | 15 | 32 | 59 | 90 | 25-50
| Brush and spray painting | 15 | 27 | 59 | 81 | 25-50
Pharmaceuticals | Manufactured powder storage and packing area | 24 | 24 | 75 | 75 | 35
| Milling room | 24 | 24 | 75 | 75 | 35
| Tablet compressing and coating | 24 | 24 | 75 | 75 | 35
| Effervescent tablets and powders | 24 | 24 | 75 | 75 | 20
| Hypodermic tablets | 24 | 24 | 75 | 75 | 30
| Colloids | 21 | 21 | 70 | 70 | 30-50
| Caught drops | 27 | 27 | 80 | 80 | 40
| Glandular products | 24 | 24 | 76 | 76 | 5-10
| Ampoule manufacturing | 24 | 24 | 75 | 75 | 35-50
| Gelatin Capsules | 24 | 24 | 76 | 76 | 35
| Capsule storage | 24 | 24 | 76 | 76 | 35
| Microanalysis | 24 | 24 | 76 | 76 | 50
| Biological manufacturing | 24 | 24 | 76 | 76 | 35
| Liver extracts | 24 | 24 | 76 | 76 | 35
| Serums | 24 | 24 | 76 | 76 | 50
| Animal rooms | 24 | 27 | 75 | 80 | 50
| Small animal rooms | 24 | 26 | 75 | 78 | 50
Paper | Binding, cutting, drying, folding, gluing | 15 | 27 | 59 | 81 | 25-50
| Storage of paper | 15 | 27 | 59 | 81 | 34-45
| Storage of books | 18 | 21 | 64 | 70 | 38-50
Plastics | Manufacturing areas thermosetting molding compounds | 27 | 27 | 80 | 80 | 25-30
| Cellophane wrapping | 24 | 27 | 75 | 80 | 45-65
Photographic | Development of film | 21 | 24 | 70 | 75 | 60
| Drying | 24 | 27 | 75 | 81 | 50
| Printing | 21 | 21 | 70 | 70 | 70
| Cutting | 22 | 22 | 72 | 72 | 65
Plywood | Hot pressing, resin | 32 | 32 | 90 | 90 | 60-70
| Cold pressing | 32 | 32 | 90 | 90 | 15-25
Printing | Binding | 21 | 21 | 70 | 70 | 45
| Folding | 25 | 25 | 77 | 77 | 65
| Pressing, general | 24 | 24 | 75 | 75 | 60-78
| Plate making | 24 | 27 | 75 | 80 | max 45
| Lithographic press room | 24 | 27 | 76 | 80 | 43-47
| Letterpress and web offset rooms | 21 | 27 | 70 | 80 | 50
| Paper storage, letterpress | 21 | 27 | 70 | 80 | 43-47
| Paper storage, multicolor sheet feed lithography | 24 | 27 | 76 | 80 | 50-55
Raw Material Storage | Nuts, insect | 7 | 7 | 45 | 45 | 65-75
| Nuts, rancidity | 1 | 3 | 34 | 38 | 65-75
| Eggs | -1 | -1 | 30 | 30 | 85-90
| Chocolate, flats | 18 | 18 | 65 | 65 | 50
| Butter | -7 | -7 | 20 | 20
| Dates, figs | 4 | 7 | 40 | 45 | 75-65
| Corn Syrup |  |  |  |  | 90-100
| Liquid sugar | 24 | 27 | 75 | 80 | 60-50
Rubber-dipped goods | Cementing | 27 | 27 | 80 | 80 | 25-30
| Dipping surgical articles | 24 | 32 | 75 | 90 | 25-30
| Storage prior to manufacture | 16 | 24 | 60 | 75 | 40-50
| Laboratory, ASTM standard | 24 | 24 | 75 | 75 | 50-55
Textile | Cotton, carding | 24 | 27 | 75 | 81 | 50
| Cotton, spinning | 15 | 27 | 59 | 81 | 60-70
| Cotton, weaving | 20 | 24 | 68 | 75 | 70-80
| Nylon, production | 27 | 27 | 81 | 81 | 50-60
| Rayon, spinning | 21 | 21 | 70 | 70 | 85
| Rayon, twisting | 21 | 21 | 70 | 70 | 65
| Silk, spinning | 24 | 27 | 75 | 81 | 65-70
| Silk, weaving | 24 | 27 | 75 | 81 | 60-70
| Wool, carding | 24 | 27 | 75 | 81 | 65-70
| Wool, spinning | 24 | 27 | 75 | 81 | 55-60
| Wool, weaving | 24 | 27 | 75 | 81 | 50-55
Tobacco | Cigar and cigarette making | 21 | 24 | 70 | 75 | 55-65
| Softening | 32 | 32 | 90 | 90 | 85
| Stemming and strigging | 24 | 30 | 75 | 86 | 70
| Filler tobacco casing conditioning | 24 | 24 | 75 | 75 | 75
| Filler tobacco storage and preparation | 26 | 26 | 78 | 78 | 70
| Wrapper tobacco storage and conditioning | 24 | 24 | 75 | 75 | 75

## airchange
Table 2 : Ventilation requirements in hospitals
Standards | ASHRAE | HTM | Singapore
Room | Minimum no. of air changes/hour
Operating Theatres | 15 | 20 | 20
Intensive Care Unit | 6 | 15 | 15
Wards (airconditioned) | 4 | - | 15
Isolation Ward (air-conditioned) | 6 | - | 15
Table 3 : Design parameters for operating theatres
Design parameters | General | Ultra-clean
1. Temperature | 20±1 °C | 20±1 °C
2. Relative Humidity | 55±5% | 55±5%
3. Bacterial count | <35 cfu/m3 | <10 cfu/m3
4. Supply air velocity at the operating table | 0.38 m/s | 0.38 m/s
5. Fresh air (no recirculation) | 20 air changes/hour | 20 air changes/hour
6. Total number of air changes | 20 air changes/hour | >300 air changes/hour
7. Pressurisation | +25 Pa | +25 Pa
8. Filtration efficiency | 99.997% at terminal | 99.997% at terminal
9. Supply air discharge area | 2.4m x 1.8m | 2.8m x 2.8m
Basement ventilation12 air changes/hr and 30 airchage/hr in case of fire
Air Changes/Hr; Constant Volume v/s VAV Volume System as per dept of Veterans usa
Areas | Minimum Design Supply Air Changes/Hr | Constant Volume (CV) or Variable Air Volume (VAV)
Animal Research Areas | 15 | CV
Ante Rooms | 12 | See Standard Detail 15900-7 or 15900-7A
Autopsy Suite (All rooms) | 12 | CV
Corridors | 4 | VAV
Dark Rooms | 10 | CV
Dialysis Rooms | 6 | CV
Dining Room | 10 | VAV
Examination Rooms | 6 | VAV
Intensive Care Units (ICUs) | 8 | CV
(All Types)
BMT Special Areas, Patient Rooms, Donor Rooms, Recovery Rooms, Medical Preparation Rooms | 18 | CV
Isolation Rooms
Aids Patient Room | 15 | CV
Burn Unit | 15 | CV
Leukemia | 15 | CV
Organ Transplant | 12 | CV
Tuberculosis | 12 | CV
Kitchens | 10 | VAV (See Article 3.12)
Laboratories
Bacteriology | 12 | CV
Biochemistry | 12 | CV
Biosafety | 12 | CV
Cytology | 12 | CV
General | 12 | CV
Histology | 12 | CV
Nuclear Medicine | 12 | CV
Pathology | 12 | CV
Special Chemistry | 12 | CV
Medical Media See Article 3.16
Minor Operating Rooms (0.R.s) (Trauma Rooms) | 12 | CV
Operating Rooms (O.R.s) | 15 (Occupied) | 8 (Unoccupied)
Patient Rooms | 4 | VAV
Recovery Rooms | 8 | CV
SPD | See Article 3.20 | CV
Special Procedure Rooms
Bronchoscopy | 12 | CV
Cardiac Catheterization | 15 | CV
Colonoscopy/EGD | 6 | CV
Cystoscopy | 15 | CV
Endoscopy | 6 | CV
Fluoroscopy | 6 | CV
GI (Gastrointestinal) | 10 | CV
Proctoscopy | 6 | CV
Sigmoidoscopy | 6 | CV
Smoking Area | 12 (Occupied) 6(Unoccupied) | CV with two settings
Storage Areas | 4 | CV
Treatment Room | 6 | VAV
Waiting Room | 6 | CV
Typical Fresh Air Requirements AS PER Blue Star
Application | Smoking | Cfm per person |  | Fresh air changes/Hr
|  | Recommended | Minimum
Apartments | Some | 20 | 15 | 1
Stores | None | 7.5 | 5 | 1
bars | Heavy | 30 | 25 | 3
Restaurants | Considerable | 15 | 12 | 2
Hotel Rooms | Considerable | 20 | 15 | 2
Conference rooms | Considerable | 20 | 15 | 3
Theatres | None | 7.5 | 5 | 3
Banks | Occasional | 10 | 7.5 | 2
Offices | Some | 15 | 10 | 1
Computer rooms | None | 10 | 7.5 | 2
Factories | None | 10 | 7.5 | 2
Fresh Air requirements & Circulation Rates for health care establishments
Type of facility | Fresh air Changes /Hr | Circulation Air Changes / hour
Operating theatre | 5 | 25
Recovery room | 2 | 6
ICU | 2 | 6
Delivery room | 5 | 12
Trauma care | 5 | 12

## noise
Noise Level Recoomendations as per dept of Veterans Washington
Type of Rooms | NC Level
Patient | 35
Examination Room, Endoscopy and Bronchoscopy | 35
Audio Suites, Audio Speech Pathology | 35
Phono/Cardiology | 35
Chapels | 40
Conference | 35
Auditorium, Theaters | 40
Operating Rooms (Major and Minor) | 35
Offices, Small Private | 40
Offices, Large Open | 35
Pharmacy | 40
Lobbies, Waiting Areas | 35
Treatment | 40
Corridors, Nurse Stations | 40
Bathrooms, Toilets | 40
Laboratories | 45
SPD, Dining, Food Service/Serving | 45
Therapeutic Pools | 45
Laundries | 50
Gymnasiums, Recreation Rooms | 50
X-Rays and General Work Rooms | 40
Laundries | 50
All Other Occupied Areas | 35-40*

## air
Temperature, density, specific heat, thermal conductivity, expansion coefficient, kinematic viscosity and Prandtl number for air at temperature between -150oC and 400oC.
Temperature | Density | Specific heat capacity | Thermal conductivity | Kinematic viscosity | Expansion coefficient | Prandtl's number
- t - | - ρ - | - cp - | - l - | ν x06 | b x 103 | Pr
| (kg/m3) | (kJ/kg.K) | (W/m.K) | (m2/s) | (1/K)
(oC)
-150 | 2.793 | 1.026 | 0.0116 | 3.08 | 8.21 | 0.76
-100 | 1.980 | 1.009 | 0.0160 | 5.95 | 5.82 | 0.74
-50 | 1.534 | 1.005 | 0.0204 | 9.55 | 4.51 | 0.725
0 | 1.293 | 1.005 | 0.0243 | 13.30 | 3.67 | 0.715
20 | 1.205 | 1.005 | 0.0257 | 15.11 | 3.43 | 0.713
40 | 1.127 | 1.005 | 0.0271 | 16.97 | 3.20 | 0.711
60 | 1.067 | 1.009 | 0.0285 | 18.90 | 3.00 | 0.709
80 | 1.000 | 1.009 | 0.0299 | 20.94 | 2.83 | 0.708
100 | 0.946 | 1.009 | 0.0314 | 23.06 | 2.68 | 0.703
120 | 0.898 | 1.013 | 0.0328 | 25.23 | 2.55 | 0.70
140 | 0.854 | 1.013 | 0.0343 | 27.55 | 2.43 | 0.695
160 | 0.815 | 1.017 | 0.0358 | 29.85 | 2.32 | 0.69
180 | 0.779 | 1.022 | 0.0372 | 32.29 | 2.21 | 0.69
200 | 0.746 | 1.026 | 0.0386 | 34.63 | 2.11 | 0.685
250 | 0.675 | 1.034 | 0.0421 | 41.17 | 1.91 | 0.68
300 | 0.616 | 1.047 | 0.0454 | 47.85 | 1.75 | 0.68
350 | 0.566 | 1.055 | 0.0485 | 55.05 | 1.61 | 0.68
400 | 0.524 | 1.068 | 0.0515 | 62.53 | 1.49 | 0.68
More about Air Composition!

## hot
Hot water Cons}mption
| Consumption per occupant |  | Peak demand per occupant |  | Storage per occupant
| liter/day | gal/day | liter/hr | gal/hr | lmter | gal
Factories (no process) | 22 - 45 | 38847 | 9 | 2 | 5 | 1
Hospitals, general | 160 | 35 | 30 | 7 | 27 | 6
Hospitals, me.tal | 110 | 25 | 22 | 5 | 27 | 6
Hostels | 90 | 20 | 45 | 10 | 30 | 7
Hotels | 90 - 160 | 00 - 35 | 45 | 10 | 30 | 7
Houses and flats | 90 - 160 | 00 - 35 | 45 | 10 | 30 | 7
Offices | 22 | 5 | 9 | 2 | 5 | 1
Schools, boarding | 115 | 25 | 20 | 4 | 25 | 5
Schools, day | 15 | 3 | 9 | 2 | 5 | 1

## duct
Air Velocity
Type of Duct | Comfort systems | Industrial systems | High speed systems
Main ducts | 4 – 7 m/s | 8 – 12 m/s | 10 – 18 m/s
Main branch ducts | 3 – 5 m/s | 5 – 8 m/s | 6 – 12 m/s
Branch ducts | 1 – 3 m/s | 3 – 5 m/s | 5 – 8 m/s
Equivalent duct sizes for rectangular and circular duct delivering air airflows at different CFM.
CFM | Equivant | Equivant Diameter
(Cubic Feet per Minute) | Rectangular Duct Sizes | Round Duct Sizes
| (Inches) | (Inches)
100 | 3 X 4 | 4
200 | 3 X 7 | 5
4 X 5
300 | 4 X 7 | 6
5 X 6
400 | 4 X 9 | 7
5 X 7
6 X 6
500 | 6 X 7 | 8
750 | 5 X 12 | 9
6 X 10
7 X 8
1000 | 7 X 10 | 10
8 X 9
1250 | 8 X 10 | 10
9 X 9
1500 | 8 X 12 | 12
10 X 10
1750 | 8 X 14 | 12
9 X 12
10 X 11
2000 | 8 X 15 | 12
10 X 12
2500 | 10 X 14 | 14
12 X 12
3000 | 12 X 14 | 14
3500 | 12 X 15 | 15
4000 | 10 X 22 | 16
14 X 15
4500 | 12 X 19 | 17
14 X 16
5000 | 10 X 25 | 17
12 X 20
15 X 16
6000 | 14 X 20 | 19
15 X 18
7000 | 12 X 26 | 20
16 X 20
8000 | 12 X 30 | 21
14 X 25
9000 | 12 X 34 | 22
15 X 25
10000 | 12 X 36 | 23
16 X 25
20 X 20
12500 | 12 X 45 | 24
16 X 30
20 X 24
15000 | 16 X 36 | 26
18 X 30
23 X 25
17500 | 16 X 40 | 28
20 X 32
25 X 25
20000 | 16 X 45 | 30
20 X 35
25 X 28
25000 | 16 X 55 | 32
20 X 43
25 X 38
30000 | 20 X 50 | 34
30 X 32
35000 | 20 X 55 | 36
30 X 35
40000 | 25 X 48 | 38
30 X 40
45000 | 25 X 25 | 40
32 X 40
50000 | 32 X 45 | 42
35 X 40

## effort
Table 1 Metabolic Rates
Activity | Metabolic Rate | Activity | Metabolic Rate
| (Met) |  | (Met)
RESTING | 0.7 | MISCELLANEOUS OCCUPATIONS | 1.4-2.0
Sleeping | 0.8 | Bakery | 1.2-2.4
Reclining | 1.0 | Brewery | 1.8-2.2
Seated, quiet | 1.2 | Carpentry | 4.0-4.8
Standing, relaxed | 2.0-3.8 | Machine sawing, table | 5.6-6.4
WALKING | 2.0-3.4 | Sawing by hand | 3.0-3.4
DOMESTIC WORK, WOMEN | 1.6-2.0 | Planning by hand | 5.0-7.0
House cleaning | 2.0-3.6 | Foundry work | 2.2-3.0
Cooking | 1.4-1.8 | Using a pneumatic hammer | 1.4-1.8
Washing by hand and ironing | 1.2-1.4 | Tending furnaces | 2.0-2.4
Shopping | 1.1-1.3 | Garage work | 3.5-4.5
OFFICE WORK | 1.1-1.3 | General laboratory work | 2.0
Typing | 1.2-2.0 | Machine work | 1.6
Miscellaneous office work | 3.0-4.0 | Light | 1.1
Drafting | 2.4-4.4 | Heavy | 1.5
LEISURE ACTIVITIES | 3.6-4.6 | Shop Assistant | 2.0
Stream fishing | 5.0-7.2 | Teacher | 3.2
Calisthenics exercise | 5.0-7.2 | Watch repairer, seated | 1.4
Dancing, social | 7.0-8.7 | Vehicle driving | 1.8
Tennis, singles | 1.4-2.6 | Car | 2.4
Squash, singles | 1.4-1.8 | Motorcycle
Basketball, half court, intramural |  | Heavy vehicle
Wrestling-competitive or intensive |  | Aircraft flying routine
Golf, swimming and walking |  | Instrument landing
Golf, swinging and golf cart |  | Combat flying

## Sheet1
Fa | Cel | Cel | Fah | Feet | meter
115 | 46.11 | 15 | 59 | 1 | 0.3
110 | 43.33 | 16 | 60.8 | 2 | 0.61
105 | 40.56 | 17 | 62.6 | 3 | 0.91
100 | 37.78 | 18 | 64.4 | 4 | 1.22
95 | 35 | 19 | 66.2 | 5 | 1.52
90 | 32.22 | 20 | 68 | 6 | 1.83
85 | 29.44 | 21 | 69.8 | 7 | 2.13
80 | 26.67 | 22 | 71.6 | 8 | 2.44
75 | 23.89 | 23 | 73.4 | 9 | 2.74
74 | 23.33 | 24 | 75.2 | 10 | 3.05
73 | 22.78 | 25 | 77 | 11 | 3.35
72 | 22.22 | 26 | 78.8
71 | 21.67 | 27 | 80.6
70 | 21.11 | 28 | 82.4
69 | 20.56 | 29 | 84.2
68 | 20 | 30 | 86
67 | 19.44 | 31 | 87.8
66 | 18.89 | 32 | 89.6
65 | 18.33 | 33 | 91.4
64 | 17.78 | 34 | 93.2
63 | 17.22 | 35 | 95
62 | 16.67 | 36 | 96.8
61 | 16.11 | 37 | 98.6
60 | 15.56 | 38 | 100.4
59 | 15 | 39 | 102.2
58 | 14.44 | 40 | 104
|  | 41 | 105.8
|  | 42 | 107.6
|  | 43 | 109.4
|  | 44 | 111.2
|  | 45 | 113

## efficiency
|  | EER | Efficacy | Cond | Evap | Efficiency
|  |  | kw/ton | 0 F | 0 F
1 | Screw Comp | 14-17 | .7-.85 | 100 | 40 | 75-82
| Part load |  | 0.42
| Screw Comp chiller package air cooled | 9 -10 | 1.06-1.15 | 100 | 40
2 | Reciprocating water | 15 | 0.79
| Reci Air cooled | 10.4-11.3 | 1.06-1.15
Recopro chiiler package air
| 20-200 tons | 9-10.9 | 1.1-1.33
| Recopro chiiler package water | 13.1-15.8 | .76-92
Screw type 120 tons carrier make
| size | 3.3 m x1 m x 1.9 m
| Chilled LPM | 1097.65
| Condensing LPM | 1722.175
| motor | 60 kw x 2 star-delta

## rh
Production and Process Environment | Recommended Relative Humidity - RH (%)
Sugar Storage | 20-35%
Breweries | 35-45%
Coffee Powder | 30-40%
Milk Powder Storage | 20-35%
Seed Storage | 35-45%
Unpacked Medicine | 20-35%
Transformer Winding | 15-30%
Semiconductors | 30-50%
Books and Paper Archive | 40-55%
Paper Storage | 35-45%
Preventing Rust and Corrosion | below 55%,
< 40% for no rust
Library | 50-55%
Spray Paint | 30-50%
Laboratory electronics | 45-60%
Plastic Pallets | 5-30%
Computer Peripherals | 50-60%
Rust Resistance | Below 40%
Medical Syrups | 30-40%
Capsule Storage | 30-45%
Powder Storage | 30-45%
Wood Drying | 25-35%
Explosives | 35-50%
Note! lower RH may cause static electricity and sparks ignition
Normal Storage | 50-55%
Musical Instrument | 45-55%
Leather Product | 40-55%
Cable Wrapping | 15-25%
Chemical Laboratory | 30-45%

## occupancy
Table Misc.-3 Occupancy
SN | Type of building | Type of room | m2 area per person
1 | Assembly building | Lecture room | 0,6
|  | Library | 5
|  | Cinema | 0,6
|  | Concert hall | 0,6
|  | Theatre | 0,6
2 | Hotel | Rooms | 5
|  | Lobby | 0,6
|  | Assembly room | 1,5
3 | Kindergarten |  | 38751
4 | Offices | Single office | 10
|  | Meeting room | 1,5
5 | Restaurant | With service | 1,5
|  | Without service | 1
6 | Schools | Lecture room | 0,6
|  | Class room | 2
|  | Corridor | 2
|  | Laboratory | 3
7 | Shop | Detail | 2
|  | Supermarket | 2
8 | Sport | Gymnasium | 1,5
|  | Swimming pool | 4

## heatgain
Table HVAC-13 : Approximate Heat Gain from Occupants in Air Conditioned Spaces.
The table below can be used to estimate the sensible and latent heat from people. The values can be used to calculate the heat load handled by the air condition system.
Degree of Activity | Typical Application | Average Metabolic rate - male adult (W) | Room Dry Bulb Temperature (oC)
|  |  | 28 |  | 27 |  | 26 |  | 24 |  | 22 |  | 20
|  |  | Sens. | Lat. | Sens. | Lat. | Sens. | Lat. | Sens. | Lat. | Sens. | Lat. | Sens. | Lat.
Seated at rest | Cinema, theatre, school | 100 | 50 | 50 | 55 | 45 | 60 | 40 | 67 | 33 | 72 | 28 | 79 | 21
Seated, very light work | Gomputer working | 120 | 50 | 70 | 55 | 65 | 60 | 60 | 70 | 50 | 478 | 42 | 84 | 36
Office work | Hotel reception, cashier | 130 | 50 | 80 | 56 | 74 | 60 | 70 | 70 | 60 | 78 | 52 | 86 | 44
Standing, walking slowly | Laboratory work | 130 | 50 | 80 | 56 | 74 | 60 | 70 | 70 | 60 | 78 | 52 | 86 | 44
Walking, seated |  | 150 | 53 | 97 | 58 | 92 | 64 | 86 | 76 | 74 | 84 | 66 | 90 | 60
Moderate work | Servant, hair dresser | 160 | 55 | 105 | 60 | 100 | 68 | 92 | 80 | 80 | 90 | 70 | 98 | 62
Light bench work | Mechanical production | 220 | 55 | 165 | 52 | 158 | 70 | 150 | 85 | 135 | 100 | 120 | 115 | 105
Moderate Dancing | Party | 250 | 62 | 188 | 70 | 180 | 78 | 172 | 94 | 156 | 110 | 140 | 125 | 125
Fast walking | Mountain walking | 300 | 80 | 220 | 88 | 212 | 96 | 204 | 110 | 190 | 130 | 170 | 145 | 155
Heavy work | Athletics | 430 | 132 | 298 | 138 | 292 | 144 | 286 | 154 | 276 | 170 | 260 | 188 | 242
Typical Application | Sensible Heat | Latent Heat
| (btu/hr) | (btu/hr)
Theater-Matinee | 200 | 130
Theater-Evening | 215 | 135
Offices, Hotels, Apartments | 215 | 185
Retail & Department Stores | 220 | 230
Drug Store | 220 | 280
Bank | 220 | 280
Restaurant | 240 | 310
Factory | 240 | 510
Dance Hall | 270 | 580
Factory | 330 | 670
Bowling Alley | 510 | 940
Factory | 510 | 940
Tabulated values are based on 78oF for dry-bulb temperature.
Adjusted total heat value for sedentary work, restaurant, includes 60 Btu/hr for food per individual (30 Btu/h sensible and 30 Btu/ latent heat).
For bowling figure one person per alley actually bowling, and all others as sitting (400 Btu/h) or standing (550 Btu/h).

## humid
Table HVAC-13 : The amount of vapor - kg per cubic meter - in humid air.
The table below can be used to estimate the amount of vapor in an air volume of 100 m3:
SN | Vapor in Air (kg per 100 m3 airflow) | Relative Humidity (%)
| Dry Temperature (oC) | 100 | 85 | 80 | 75 | 70 | 65 | 60 | 55 | 50 | 45 | 40 | 35 | 30
1 | 32 | 3.39 | 2.89 | 2.72 | 2.55 | 2.38 | 2.19 | 2.04 | 1.93 | 1.7 | 1.53 | 1.36 | 1.19 | 1.02
2 | 31 | 3.22 | 2.73 | 2.57 | 2.41 | 2.25 | 2.1 | 1.93 | 1.77 | 1.61 | 1.45 | 1.29 | 1.13 | 0.97
3 | 30 | 3.05 | 2.59 | 2.44 | 2.29 | 2.13 | 1.97 | 1.83 | 1.67 | 1.52 | 1.37 | 1.22 | 1.07 | 0.91
4 | 29 | 2.89 | 2.45 | 2.31 | 2.17 | 2.02 | 1.88 | 1.73 | 1.59 | 4.45 | 1.3 | 1.16 | 1.01 | 0.87
5 | 28 | 2.73 | 2.32 | 2.19 | 2.05 | 1.91 | 1.78 | 1.64 | 1.5 | 1.37 | 1.23 | 1.1 | 0.96 | 0.82
6 | 27 | 2.59 | 2.2 | 2.07 | 1.94 | 1.81 | 1.68 | 1.55 | 1.42 | 1.29 | 1.16 | 1.03 | 0.91 | 0.78
7 | 26 | 2.45 | 2.08 | 1.96 | 1.83 | 1.71 | 1.59 | 1.47 | 1.34 | 1.22 | 1.1 | 0.97 | 0.86 | 0.73
8 | 25 | 2.31 | 1.97 | 1.85 | 1.73 | 1.62 | 1.5 | 1.39 | 1.27 | 1.16 | 1.04 | 0.93 | 0.81 | 0.69
9 | 24 | 2.19 | 1.86 | 1.75 | 1.64 | 1.53 | 1.42 | 1.31 | 1.2 | 1.09 | 0.98 | 0.87 | 0.77 | 0.66
10 | 23 | 2.06 | 1.76 | 1.63 | 1.55 | 1.45 | 1.34 | 1.24 | 1.14 | 1.03 | 0.93 | 0.83 | 0.72 | 0.62
11 | 22 | 1.95 | 1.66 | 1.56 | 1.46 | 1.36 | 1.27 | 1.17 | 1.07 | 0.98 | 0.88 | 0.78 | 0.68 | 0.59
12 | 21 | 1.84 | 1.56 | 1.47 | 1.38 | 1.29 | 1.2 | 1.1 | 1.02 | 0.92 | 0.83 | 0.74 | 0.67 | 0.55
13 | 20 | 1.74 | 1.48 | 1.39 | 1.3 | 1.22 | 1.13 | 1.04 | 0.98 | 0.87 | 0.78 | 0.69 | 0.61 | 0.52
14 | 19 | 1.63 | 1.39 | 1.31 | 1.23 | 1.15 | 1.06 | 0.98 | 0.9 | 0.82 | 0.74 | 0.65 | 0.57 | 0.49
15 | 18 | 1.54 | 1.31 | 1.24 | 1.16 | 1.08 | 1 | 0.93 | 0.85 | 0.77 | 0.69 | 0.62 | 0.54 | 0.46
16 | 17 | 1.45 | 1.24 | 1.16 | 1.09 | 1.02 | 0.94 | 0.87 | 0.8 | 0.73 | 0.65 | 0.59 | 0.51 | 0.44
17 | 15 | 1.29 | 1.1 | 1.03 | 0.97 | 0.9 | 0.84 | 0.77 | 0.71 | 0.66 | 0.58 | 0.52 | 0.45 | 0.39
18 | 10 | 0.94 | 0.8 | 0.76 | 0.71 | 0.66 | 0.61 | 0.57 | 0.52 | 0.47 | 0.43 | 0.38 | 0.33 | 0.28
19 | 0 | 0.49 | 0.41 | 0.39 | 0.37 | 0.34 | 0.32 | 0.29 | 0.27 | 0.24 | 0.22 | 0.2 | 0.17 | 0.15
20 | -5 | 0.33 | 0.28 | 0.26 | 0.25 | 0.23 | 0.21 | 0.2 | 0.18 | 0.16 | 0.15 | 0.13 | 0.11 | 0.1
21 | -10 | 0.22 | 0.18 | 0.17 | 0.16 | 0.15 | 0.14 | 0.13 | 0.12 | 0.11 | 0.1 | 0.09 | 0.08 | 0.06
Note! In psychrometric charts and Mollier diagram the amount of vapor is given in kg/kg dry air. The values from the table above can be transformed dividing by the air density at the actual temperature.
Example - Humidifying Air with Steam
Air at 20oC and 30% relative humidity are humidified to 20oC and 80% relative humidity.
From a table above air at 20oC and 30% relative humidity contains 0.52 kg water vapor per 100 m3 air flow. Air at 20oC and 80% relative humidity contains 1.39 kg per 100 m3 air flow.
The amount of water vapor needed can be calculated as:
Amount of Water Vapor = ((1.39 kg) - (0.52 kg))
= 0.87 kg is the amount of water vapor necessary for an air volume of 100 m3.

## water
[5 empty] | Type of Fitting | Consumption
[6 empty] | liter/h | gal/h
[5 empty] | Basin (private) | 14 | 3
| Type of fitting | Storage Capacity |  |  | Basin (public) | 45 | 10
|  | liters | gal |  | Shower | 180 | 40
| Basin | 90 | 20 |  | Sink | 45-90 | 10-20
| Bath | 900 | 200 |  | Bath | 90-180 | 20-40
| Garden watering tap | 180 | 40
| Shower | 450 - 900 | 100 - 200
| Sink | 90 | 20
| Urinal | 180 | 40
| WC | 180 | 40
below can be used to determine the maximum numbers of draw offs served by a pipe:
Nominal bore of pipe |  |  | Maximum number of draw offs served
|  |  | Flow pipes |  | Return pipes
in | Steel pipe | Copper pipe | Head up to 20 m | Head over 20 m
| (mm) | (mm) | (70 ft) | (70 ft)
1/2 | 15 | 15 | 1 | 1 - 2 | 1 - 8
3/4 | 20 | 22 | 2 - 4 | 3 - 9 | 9 - 29
1 | 25 | 28 | 5 - 8 | 10 - 19 | 30 - 66
1 1/4 | 32 | 35 | 9 - 24 | 20 - 49 | 67 - 169
1 1/2 | 40 | 42 | 25 - 49 | 50 - 79 | 170 - 350
2 | 50 | 54 | 50 - 99 | 80 - 153
2 1/2 | 65 | 67 | 100 - 200 | 154 - 300
Basins, Zinks, showers and similar are regarded as 1 draw off
Baths and similar are regarded as 2 draw offs

## fan
Fan discharge velocities for quiet operation
Application | Supply | Extract
| systems | systems
| m/s | m/s
Sound studios, churches, libraries | 4-5 | 5-7
Cinemas, theatres, ballrooms | 5 - 7,5 | 6-8
Restaurants, offices, hotels, shops | 6-8 | 7-9

## ref
Table HVAC-14 : Properties of Refrigerants
SN | Refrigerant | Formula | Boiling Temp. | Critical Temp. | Properties | Applications
|  |  | oC | oC
| Ammonia | NH3 | -33 | 133 | Penetrating odour, soluble in water. harmless in concentration up to 1/30%, non flammable, explosive | Large industrial plants
| R12 | C Cl2F2 | -29,8 | 112 | Little odour, colourlessas gass or liquid, non flammable, non corrosive of ordinary metals, stable | Small plants with reciprocating compressors.
| R11 | C Cl3F | 8,9 | 198 | Non flammable, non corrosive non toxic, stable | Commercial plants with centrifugal compressors.
| R22 | CH Cl F2 | -40,8 | 96 | Little odour, colourless as gas or liquid, non toxic, non irritating, non flammable, non corrosive, stable | Packaged airconditioning units where size of equipment and economy are important.
| R500 | C Cl2 F2 (73,8%) | -33 |  | Simmilar to R12 | Offers aprox. 20% more refrigeration capacity than R12 for same compressor.
CH3 CH F2 (26.2%)
| R502 | C Cl F2 (48,8%) + F2 - CF3 (51.2%) | -45,6 | 90,1 | Non flammable, non toxic, non corrosive, stable | Capacity comparable to R22.
| R134a | Tetrafluoroethane (CF3CH2F) | -26.1°C. |  | It is safe for normal handling as it is non-toxic, non-flammable and non-corrosive. | Used as a replacement for R-12 CFC refrigerant in the area of centrifugal, rotary screw, scroll andreciprocating compresssors.
Properties of R-134a
|  |  |  | No | Properties | R-134a
|  |  |  | 1 | Boiling Point | -14.9°F or -26.1°C
|  |  |  | 2 | Auto-Ignition Temperature | 1418°F or 770°C
|  |  |  | 3 | Ozone Depletion Level | 0
|  |  |  | 4 | Solubility In Water | 0.11% by weight at 77°F or 25°C
|  |  |  | 5 | Critical Temperature | 252°F or 122°C
|  |  |  | 6 | Cylinder Color Code | Light Blue
|  |  |  | 7 | Global Warming Potential (GWP) | 1200
Latest Development
The recent discovery that R-134a contributes to global warming has caused the European Union to ban its use on new carsstarting from year 2011. Other countries are expected to follow suit.
Refrigerants related to HFCs group
R 125 refrigerant. Chemical formula СНF2СF3
Related to HFC group, it does not contain chlorine. Ozone depletion potential ODP = 0, global warming potential GWP = 860. Boiling point at the atmospheric pressure is -48,1 oС. The refrigerant is reccomended to use in a clear type or as a component of alternative blends to substitute R22, R502 and R12. R125 refrigerant is fire safe. As to energy performance and heat-transfer coefficient, it plays back to R22 and R502 refrigerants. Compared to R502, it has more abrupt curve characterizing dependence of saturated vapors pressure on temperature, low critical temperature and not high specific temperature of heat-vapor buildup which causes the necessity of increase of the compression level. In connection with this, possibilities of R125 use in the refrigeration equipment using condensers with air cooling are extremely limited.
At the same time, R125 has lower (compared to R22 and R502) discharge temperature and high mass flow under low suction pressures. Piston refrigeration compressors operating on R125 are characterized by optimal cylinder charging, and as a consequence, they have big volume efficiency.
R134a refrigerant. Chemical formula CF3CFH2 (tetrafluoroethane).
R134a molecule has smaller size than R12 molecule which makes danger of leakage more considerable. Related to HFC group. Ozone depletion potential ODP = 0, global warming potential GWP = 1300.
R134a refrigerant is non-toxic and does not flare up within the whole range of operational temperatures. However, in case of air ingress into the system and compression there can be formed combustible blends. You shouldn't mix R134a with R12 because there is formed azeotrope blend of high pressure with mass proportions of the components 50 and 50%. Saturated vapor pressure of this refrigerant is a bit higher than that of R12 (correspondingly 1,16 and 1,08 МPа at 45 oС). R134a vapor is decomposed under the influence of flame with formation of poisonous and irritating contextures, such as fluorohydrogen.
According to classification ASHRAE, this product is related to class А1. In middle-temperature equipment (boiling point -7 oС and higher), R134a has operation performance close to R12.
R134a is characterized by not high discharge temperature (it is approximately 8...10oС lower than for R12) and not high values of saturated vapors pressure.
In refrigeration facilities operating under boiling point lower than -15 oС, energy data of R134a are worse than those of R12 ( specific volumetric refrigerating effect is 6% lower at -18 oС), and refrigerating factor. In such facilities it is purposeful to use refrigerants with lower normal boiling point or compressor with increased time volume circumscribed by pistons.
In middle temperature refrigeration facilities and air-conditioning systems, refrigerating factor of R134a is equal to the factor for R12 or higher than that.
In high-temperature refrigeration facilities, specific cold-productivity when operating on R134a is also a bit higher (6% more at tо = t0 oС), than that of R12. Ranges of using R134a refrigerant are shown in Fig., and dependence of cold-productivity and refrigerating factor on boiling point is shown further on the figure.
Due to considerable global warming potential GWP, it is recommended to use R134a in hermetic refrigerating systems. Contribution of R134a to greenhouse effect is 1300 times as bigger as that of СО2. Thus, air venting of R134a one filling from a domestic refrigerator (about 140 gm) corresponds to ejection of 170 kg of СО2. In Europe about 448 gm of СО2 is formed at production of 1 kWt/h of power, that is, this ejection corresponds to production of 350 kWt*h of power.
For operation with R134a refrigerant, only polyester refrigeration oils characterized by increased hygroscopic property are recommended.
R134a is widely used all over the world as a main substitute of R12 fir refrigeration equipment operating within middle-temperature range. It is used in automobile air-conditioners, domestic refrigerators, commercial refrigeration middle-temperature equipment, industrial facilities, air-conditioning systems in buildings and industrial areas, as well as on refrigeration transport. The refrigerant can be used also for retrophite of the equipment operating at lower temperatures. However, in this case, if the compressor is not substituted, refrigeration system can have reduced cold-productivity.
R134a is compatible with a number of sealing materials, in particular, with pads made of such materials as "Buna-N", "Khailalon 48", "Neopren", "Nordel". As the analysis carried out by company "Du Pont" showed, change of mass and linear swelling of such materials used in domestic refrigeration equipment as phenoplast and polyamide chocks, textolite, paronite and polyethylene terephtalate skins, in combination of SUVA R134a with polyester oil "Castrol SW100" at 100 oС during 2 weeks have been insignificant.
R134a is compatible with a number of sealing materials, in particular, with pads made of such materials as "Buna-N", "Khailalon 48", "Neopren", "Nordel". As the analysis carried out by company "Du Pont" showed, change of mass and linear swelling of such materials used in domestic refrigeration equipment as phenoplast and polyamide chocks, textolite, paronite and polyethylene terephtalate skins, in combination of SUVA R134a with polyester oil "Castrol SW100" at 100 oС during 2 weeks have been insignificant.
Analysis of foreign publications and the results of the research of native specialists indicate that substitution of R12 for R134a, which has high global warming potential GWP, in refrigeration compressors is connected with solution of a number of technical tasks basic of which are:
Improvement of volume and energy performance of hermetic compressors;
Increasing of chemical constancy of enamel wires of the hermetic compressor electric motor;
Increasing of dehumidifying ability of filter-dehydrators due to high hygroscopic property of R134a system - synthetic oil.
All this should result in considerable increase of the cost of refrigeration equipment. At the same time, in water-cooling plants with screw and centrifugal compressors the use of R134a has certain perspectives.
R 143a refrigerant. Chemical formula CF3-СН3 (trifluoroethane)
R143a has ozone depletion potential ODP = 0 and comparatively high global warming potential GWP = 1000, non-toxic and fire-safe, it does not interact with structural and packing materials. Three hydrogen atoms in R143a molecule contribute to good solubility in mineral oils. Specific heat of vaporization is 19,88 kJoule/mole at normal boiling point which is a bit higher than for R125 (18,82 kJoule/mole). Discharge temperature is lower than that of R12, R22 and R502. As energy analysis has showed, energy effectiveness of two-step cycle with R143a is close to the effectiveness of the cycle with R502, lower than that of R22, and higher than that of R125. R143a refrigerant belongs to composition of multi-component alternative blends suggested for substitution of R12, R22 and R502.
R 32 refrigerant. Chemical formula CF2H2 (difluoromethane).
Related to HFC group. R32 has ozone depletion potential ODP = О and low global warming potential GWP = 220, in comparison with R125 and R143a. Non-toxic, fire risky. It has high specific heat of vaporization 20,37 kJoule/mole at normal boiling point and abrupt dependence of saturated vapors pressure on the temperature and, as a result, R32 is characterized by high discharge temperature, which is the highest of all alternative refrigerants, except ammonia. R32 is soluble in polyester oils.
When used in refrigeration facilities, R32 is characterized by high cold-productivity and energy effectiveness, but it is slightly inferior to R22 and R717. High level of R32 compression causes necessity of considerable alteration in the refrigeration facility design at retrophite, and as a consequence, it results in increasing of its metal intensity and cost. Therefore, R32 is recommended to use mainly as a component of alternative working blend. Due to small size of R32 molecule compared to molecules of ethane row refrigerants, R32 selective leakage through looseness in the refrigerating system is possible, which can change the composition of multi-component working blend.

## fresh
Minimum Outdoor Air Requirements
Rooms | Outdoor Air
2 Air Changes/Hr, or 10 Air Changes/Hr of Make-up Air for the Adjoining Toilets/ Bathrooms, or 0.85 Cu M/Min (30 CFM) Per Patient.
Patient Bedrooms
Offices (Private) | 1 Air Change/Hr, or 0.56 Cu M/Min (20 CFM) Per Person.
Lounge/Waiting Areas | 0.42 Cu M/Min (15 CFM) Per Person.

## filter
Table HVAC 15 : Filter Efficiencies (percent) for all Air systems
SN | Area Served | (Efficiency)
|  | Pre-filters (Efficiency) | After-filters
1 | Animal Holding Areas | 30 | 85
2 | Animal Operating Rooms | 30 | 95
3 | Administrative areas, conference rooms, and lobbies | 15 | 60
4 | Auditoriums, Chapels, and Theaters | 15 | 60
5 | Autopsy Suite exhaust | 30 | 99.97; HEPA Filters
6 | Autopsy Suites supply air | 30 | 85
7 | BMT Suites | 30 | 99.97; HEPA Filters
8 | Burn Unit | 30 | 99.97; HEPA Filters
9 | Clean supplies and processing areas | 30 | 85
10 | Dental Clinics | 30 | 85
11 | Dialysis Rooms | 30 | 85
12 | Dietetics (Kitchen and Dining areas) | 15 | 60
13 | Emergency Care Units (Ambulatory Care} | 30 | 85
14 | Gymnasium | 15 | 60
15 | Heat recovery Units (In exhaust air on upstream side of the coil) | 30 | -
16 | Human Immunodeficiency Virus (HIV) | 30 | 99.97; HEPA Filters
17 | ICUs utilizing return air system | 30 | 99.97; HEPA Filter
18 | ICUs and Recovery Rooms in surgical suite | 30 | 95
19 | Isolation Room exhausts. For TB isolation, see Article 3.22 | 30 | 99.97; HEPA Filters
20 | Laboratories, supply system | 30 | 85
21 | Laundries, soiled holding areas, and bulk storage | 30 | -
22 | MRI, CT Scanners, and Linear Accelerators | 30 | 85
23 | Nuclear Medicine | 30 | 85
24 | Operating Rooms, and Trauma rooms | 30 | 95
25 | Orthopedic Surgery | 30 | 99.97; HEPA Filters
26 | Medical Media | 30 | 85
27 | Make-up units for lab and kitchen range hood | 30 | -
28 | Patient Bed Rooms | 30 | 85
29 | Patient care such as examination, and treatment areas. | 30 | 85
30 | Pharmacy | 30 | 85
31 | Radiation Therapy | 30 | 85
32 | Radiology | 30 | 85
33 | Special Procedure Rooms | 30 | 85
34 | Spinal Card Injury Unit (SCIU) | 30 | 85
35 | SPD | 30 | 85
36 | Warehouses | 30 | -

## exhaust
Table HVAC-18 : Minimum Exhaust Air Requirements/Room Pressure
SN | Areas | Room Pressure | Exhaust Air Air Changes/Hr
| Admitting and Waiting Areas | Negative | SA + 15 Percent of SA
| Ambulance Entrance | Negative | 10
| Animal Research | Negative | SA + 15 Percent of SA
| Ante Rooms | See Standard Detail 15900-7 or 15900-7A
| Autopsy Suite (All Rooms) | Negative | SA + 15 Percent of SA
| Battery Charging Areas | Negative | 8
| Bathing Facilities | Negative | 10
| Bathrooms | Negative | 10
| BMT Patient Areas | Positive | SA – 15 Percent of SA
| Ceramics Rooms (dental Prosthetics Laboratories) | Positive | SA – 15 Percent of SA
| Clean and Preparation Rooms (SPD Suites) | Positive | SA – 15 Percent of SA
| Clean Rooms (Laundry Facilities) | Positive | SA – 15 Percent of SA
| Dark Rooms | Negative | SA + 15 Percent of SA
| Detergent Storage | Negative | SA + 15 Percent of SA
| Dialysis | Positive | SA – 15 Percent OF SA
| Dietetics {See Note (a)} | Negative | SA + 15 Percent of SA
| Enema or Hopper Rooms | Negative | 15
| Examination Rooms (MRI Suites) | Equal | 12
| Flammable Storage | Negative | 0.3 Cu M/Min/0.1 Sq M, 4.2 Cu M/Min Minimum (1.0 CFM/Sq Ft, 150 CFM Minimum)
| Gas Storage | Negative | 0.3 Cu M/Min/0.1 Sq M, 4.2 Cu M/Min Minimum (1.0 CFM/Sq Ft, 150 CFM Minimum)
| Glass and Cage Washing Areas | Negative | See Notes
| Instrument Rooms (Sterile) | Positive | SA – 15 Percent of SA
| Intensive Care Units (ICUs) | Positive | SA – 15 Percent of SA See Article 3.10
| Isolation Rooms (Negative Pressure) | See VA STD Detail 15900-7 | SA + 15 Percent of SA
(All Articles listed in Table 3-5 and Table 3-6) and paragraph 2.11.6
| Isolation Rooms (Positive Pressure) | See VA STD Detail 15900-7A
| Aids Patient Rooms | Positive | SA – 15 Percent of SA
| Burn Units | Positive | SA – 15 Percent of SA
| Leukemia Patient Rooms | Positive | SA – 15 Percent of SA
| Organ Transplant Rooms | Positive | SA – 15 Percent of SA
| Janitor Closet (HAC) | Negative | 10
| Kitchen (See Note b) | Negative | SA + 15 Percent of SA
| Laboratories | Negative | SA + 15 Percent of SA See Article 3.13
| Laundry (Central Facility) | Negative | See Article 3.14
| Locker Rooms {See Note (c)} | Negative | SA + 15 Percent
See Note (c)
Medical Media Service (MMS) See Article 3.16
| Minor Operating Rooms (O.R.s) (Trauma Rooms) | Positive | See Article 3.1.2
| Operating Rooms (Surgery Suites) | Positive | See Article 3.21
| Oral Surgery and Treatment | Positive | SA – 15 Percent of SA
| Radiation Therapy | Negative | SA + 15 Percent of SA
| Reagent Grade Water Treatment Rooms | Negative | 8
| Recovery Rooms | Positive | SA – 15 Percent of SA
| Silver Recovery Rooms | Negative | 6
| Smoking Area | Negative | 12
| Soiled Dishwashing Rooms | Negative | 6
| Soiled Linen Rooms | Negative | 6
| Soiled Utility Rooms | Negative | 6
Special Procedure Rooms
| Bronchoscopy | Negative | SA + 15 Percent of SA
| Cardiac Catheterization | Positive | SA – 15 Percent of SA
| Colonoscopy/EGD | Negative | SA + 15 Percent of SA
| Cystoscopy | Positive | SA – 15 Percent of SA
| Endoscopy | Negative | SA + 15 Percent of SA
| Fluoroscopy | Negative | SA + 15 Percent of SA
| GI (Gastrointestinal) | Negative | SA + 15 Percent of SA
| Proctoscopy | Negative | SA + 15 Percent of SA
| Sigmoidoscopy | Negative | SA + 15 Percent of SA
Sterile Corridors (Surgery Suites) See Article 3.21
| Storage Rooms (Soiled or Dirty) | Negative | SA + 15 Percent of SA
| Tissue Culture Rooms | Positive | SA – 15 Percent of SA
| Toilets | Negative | 10
| Treatment Room (Bronchoscopy) | Negative | SA + 15 Percent of SA
| Trash Collection Areas | Negative | 10
| Vestibules | Positive | SA – 15 Percent of SA
| Waiting Rooms | Negative | SA + 15 Percent of SA