## indoor
Table 1-1 Indoor Design Conditions
Recoomendations as per dept of Veterans Washington
| Summer |  |  | Winter
| Db Degrees C (Degrees F) |  | RH Percent | Db Degrees C (Degrees F) | RH Percent
Animal Research (Animal Rooms) | 18 (65) |  | 60 (+5) | 29 (85) | 30 (+5)
Auditoriums | 24 (76) |  | 60 | 22 (72) | --
AIDS Patient Areas | 24 (76) |  | 50 | 25 (78) | 30
Autopsy Suites | 24 (76) |  | 60 | 24 (76) | 30
Bathrooms & Toilet Rooms | 25 (78) |  | -- | 22 (72) | --
Blood Banks | 22 (72) |  | 50 | 22 (72) | 30
BMT (Bone Marrow Transplant) Patient Areas | 24 (76) |  | 50 | 25 (78) | 30
Computer Rooms | 21 (70) |  | 40 (+5) | 21 (70) | 40 (+5)
CT Scanner | 24 (76) |  | 50 | 25 (78) | 30
Dialysis Rooms | 25 (78) |  | 50 | 22 (72) | 30
Dining Rooms | 25 (78) |  | 50 | 22 (72) | 30
Dry Labs | 25 (78) |  | 50 | 22 (72) | 30
Electrical Equipment Rooms | Ventilation Only |  |  | 10 (50) | --
Elevator Machine Rooms, Electric Drive | 36 (94) |  | -- | 10 (50) | --
Elevator Machine Rooms, Hydraulic | 36 (94) |  | -- | 10 (50) | --
Emergency Generator | 42 (110) |  | -- | 4 (40) | --
Examination Rooms | 24 (76) |  | 50 | 25 (78) | 30
Gymnasiums | Ventilation Only |  |  | 21 (70) | --
ICUs (Coronary, Medical, Surgical) | 23–29 (75–85) |  | 30–60 | 23–29 (75–85) | 30-60
Isolation Suites | 24 (76) |  | 50 | 25 (78) | 30
Kitchens | 27 (82) |  | 60 | 21 (70) | --
Laboratories | 24 (76) |  | 50 | 22 (72) | 30
Laundries | 28 (84) |  | 60 | 19 (68) | -
Linear Accelerators | 24 (76) |  | 50 | 25 (78) | 30
Locker Rooms | 25 (78) |  | 50 | 22 (72) | 30
Lounges | 25 (78) |  | 50 | 22 (72) | 30
Mechanical Equipment Rooms (MERs) | Ventilation Only |  |  | 10 (50) | --
Medical Media: See Article 3.16
Minor O.R.s (Trauma Rooms) |  | 24 (76) | 50 | 25 (78) | 30
Motor Vehicle Maintenance/Storage |  | Ventilation Only |  | 21 (70) | --
MRI Units |  | 24 (76) | 50 | 25 (78) | 30
Offices, Conference Rooms |  | 25 (78) | 50 | 22 (72) | 30
Operating Rooms (O.R.s) |  | 17–27 (62-80) | 45-55 | 17-27 (62-80) | 45-55
Operating Rooms (O.R.s) - Animal |  | 22 (73) | 50 | 22 (73) | 50
Patient Rooms |  | 24 (76) | 50 | 25 (78) | 30
Pharmacy |  | 22 (72) | 50 | 22 (72) | 30
Radiation Therapy |  | 24 (76) | 50 | 25 (78) | 30
Recovery Units |  | 23 (75) | 50 | 23 (75) | 30
Smoking Area |  | 25 (78) | 50 | 22 (72) | 30
SPECIAL PROCEDURE ROOMS*
Bronchoscopy | 24 (76) |  | 50 | 25 (78) | 30
Cardiac Catheterization | 17–27 (62-80) |  | 45-55 | 17-27 (62-80) | 45-55
Colonoscopy/EGD | 24 (76) |  | 50 | 25 (78) | 30
Cystoscopy | 22 (72) |  | 50 | 25 (78) | 50
Endoscopy | 24 (76) |  | 50 | 25 (78) | 30
Fluoroscopy | 24 (76) |  | 50 | 25 (78) | 30
GI (Gastrointestinal) | 24 (76) |  | 50 | 25 (78) | 30
Proctoscopy | 24 (76) |  | 50 | 25 (78) | 30
Sigmoidoscopy | 24 (76) |  | 50 | 25 (78) | 30
Spinal Cord Injury Units (SCIUs) | 22 (72) |  | 50 | 27 (82) | 30
Supply Processing Distribution (SPD) | 24 (76) |  | 50 | 22 (72) | 30
Ethylene Oxide (ETO) MERs | Ventilation only
Steam Sterilizer MERs | Ventilation only
Telephone Equipment Rooms | 19(65)-23(75) |  | 40-60 | 19(65)-23(75) | 40-60
Therapeutic Pools | 26(80)-29(85) |  | -- | 29 (85) | --
Transformer Rooms | 39 (104) |  | (Maximum)
Treatment Rooms | 24 (76) |  | 50 | 25 (78) | 30
Warehouses | Ventilation Only |  |  | 15 (60) | --
Table 1 : Temperature and humidity requirements in hospitals
Standards | ASHRAE | HTM | Singapore | ASHRAE | HTM | Singapore
Room | Temperature (°C) |  |  | Relative Humidity (%RH)
Operating Theatres | 17~27 | 15~25 | 19- 21 | 45~55 | 40~60 | 50~60
Intensive Care Unit | 24~27 | - | 22-23 | 30~60 | - | 55~65
Wards (airconditioned) | 24 | - | 22~23 | 30~60 | - | 55~65
Isolation Ward | 24~27 | - | 22~23 | 30~60 | - | 55~65
Industry | Process | Temperature oC min | Temperature oC max | Temperature oF min | Temperature oF max | Relative humidity %
Abrasives | Manufacturing | 26 | 26 | 79 | 79 | 50
Ammunition |  | 21 | 21 | 70 | 70 | 40
Bakery | Flour storage | 16 | 26 | 61 | 79 | 55-65
| Production | 23 | 26 | 73 | 79 | 40-70
Billiard Room |  | 23 | 24 | 73 | 75 | 40-50
Bowling Center | Bowling alleys | 23 | 24 | 73 | 75 | 50- 55
| Billiard rooms | 23 | 24 | 73 | 75
Bread | Flour and powdered storage | 21 | 27 | 70 | 80 | 60
| Fermentation | 27 | 27 | 80 | 80 | 75
| Retarding of Dough | 0 | 4 | 32 | 40 | 85
| Final Proof | 35 | 49 | 95 | 120 | 85-90
| Counter flow Cooling | 24 | 24 | 75 | 75 | 80-85
Brewing | Hop storage | -2 | 0 | 29 | 32 | 50-60
| Yeast culture room |  |  |  |  | 80
Candy | Chocolate Pan supply air | 13 | 17 | 55 | 62 | 55-45
| Enrobed room | 27 | 29 | 80 | 85 | 30-25
| Chocolate Cooling Tunnel supply air | 4 | 7 | 40 | 45 | 85-70
| Hand Dippers | 17 | 17 | 62 | 62 | 45
| Molded goods cooling | 4 | 7 | 40 | 45 | 85-70
| Chocolate Packing room | 18 | 18 | 65 | 65 | 50
| Chocolate finished stock storage | 18 | 18 | 65 | 65 | 50
| Centers tempering room | 24 | 27 | 75 | 80 | 35-30
| Marshmallow setting room | 24 | 26 | 75 | 78 | 45-40
| Grained marshmallows drying | 43 | 43 | 110 | 110 | 40
| Gum drying | 52 | 66 | 125 | 150 | 25-15
| Sanded Gum drying | 38 | 38 | 100 | 100 | 25-40
| Gum finished stock storage | 10 | 18 | 50 | 65 | 65
| Sugar pan supply air | 29 | 41 | 85 | 105 | 30-20
| Polishing pan supply air | 21 | 27 | 70 | 80 | 50-40
| Pan rooms | 24 | 27 | 75 | 80 | 35-30
| Nonpareil Pan supply air | 38 | 49 | 100 | 120 | 20
| Hard candy cooling tunnel air | 16 | 21 | 60 | 70 | 55-40
| Hard candy packing | 21 | 24 | 70 | 75 | 40-35
| Hard candy storage | 10 | 21 | 50 | 70 | 40
| Caramel rooms | 21 | 27 | 70 | 80 | 40
Ceramics | Refractory | 43 | 66 | 110 | 150 | 50-90
| Molding room | 27 | 27 | 80 | 80 | 60-70
| Clay storage | 16 | 27 | 60 | 80 | 35-65
| Decalcomania production | 24 | 27 | 75 | 80 | 50
| Decoration room | 24 | 27 | 75 | 80 | 50
Cereal | Packaging | 24 | 27 | 75 | 80 | 45-50
Cheese Curing | Cheddar | 7 | 13 | 45 | 55 | 85-90
| Swiss | 16 | 16 | 60 | 60 | 80-85
| Blue | 9 | 10 | 48 | 50 | 95
| Brick | 16 | 18 | 60 | 65 | 90
| Limburger | 16 | 18 | 60 | 65 | 95
| Camembert | 12 | 15 | 53 | 59 | 90
Clean rooms |  | 21 | 27 | 70 | 80 | 40-60
Distilling | Grain Storage | 16 | 16 | 60 | 60 | 35-40
| General Manufacturing | 16 | 24 | 60 | 75 | 45-60
| Aging | 18 | 22 | 65 | 72 | 50-60
Fruit Storage | Apples | -1 | 4 | 30 | 40 | 90
| Apricots | -1 | 0 | 31 | 32 | 90-95
| Grapefruits (California) | 14 | 16 | 58 | 60 | 85-90
| Grapefruits (Florida) | 10 | 10 | 50 | 50 | 85-90
| Grapes (Eastern) | -1 | 0 | 31 | 32 | 85
| Grapes (Western) | -1 | -1 | 30 | 31 | 90-95
| Lemons | 14 | 16 | 58 | 60 | 86-88
| Oranges (California) | 4 | 7 | 40 | 44 | 85-90
| Oranges (Florida) | 0 | 1 | 32 | 34 | 85-90
| Peaches and Nectarines | -1 | -1 | 31 | 31 | 90
| Plums | -1 | 0 | 30 | 32 | 90-95
| Citrus fruits | 3 | 4 | 38 | 40 | 90-95
Fur | Storage | -2 | 4 | 28 | 39 | 25-40
| Drying | 43 | 43 | 109 | 109
Gum | Manufacturing | 25 | 25 | 77 | 77 | 33
| Rolling | 20 | 20 | 68 | 68 | 63
| Stripping | 22 | 22 | 72 | 72 | 53
| Breaking | 23 | 23 | 74 | 74 | 47
| Wrapping | 23 | 23 | 74 | 74 | 58
Hospitals | Operating, Cystoscopic and fracture rooms | 20 | 24 | 68 | 76 | 50
| Patient rooms | 24 | 24 | 75 | 75 | 40-50
| Intensive care unit | 24 | 24 | 75 | 75 | 40
| Administrative and service areas | 21 | 27 | 70 | 80 | 30-50
Leather | Drying | 21 | 49 | 70 | 120 | 75
| Storage, winter room temperature | 10 | 16 | 50 | 60 | 40-60
Lenses (optical) | Fusing | 24 | 24 | 75 | 75 | 45
| Grinding | 27 | 27 | 80 | 80 | 80
Libraries and Museums | Normal reading and viewing rooms | 21 | 23 | 70 | 74 | 40-50
| Rare manuscript and Storage Vaults | 21 | 22 | 70 | 72 | 45
| Art Storage Areas | 18 | 22 | 65 | 72 | 50
Matches | Manufacture | 22 | 23 | 72 | 74 | 50
| Drying | 21 | 24 | 70 | 75 | 60
| Storage | 16 | 17 | 60 | 62 | 50-55
Meat and fish | Beef (fresh) | 0 | 1 | 32 | 34 | 88-92
| Beef (frozen) | -23 | -18 | -10 |  | 90-95
| Fish (fresh) | 1 | 2 | 33 | 35 | 90-95
| Fish (Frozen) | -23 | -18 | -10 |  | 90-95
| Lamb and Pork (Fresh) | 0 | 1 | 32 | 34 | 85-90
| Lamb and Pork (Frozen) | -23 | -18 | -10 |  | 90-95
Mushrooms | Sweating out period | 49 | 60 | 120 | 140
| Spawn added | 16 | 24 | 60 | 75 | 100
| Growing period | 9 | 16 | 48 | 60 | 80
| Storage | 0 | 2 | 32 | 35 | 80-85
Paint Applications | Oil paint spraying | 16 | 32 | 60 | 90 | 80
| Drying oil paints | 15 | 32 | 59 | 90 | 25-50
| Brush and spray painting | 15 | 27 | 59 | 81 | 25-50
Pharmaceuticals | Manufactured powder storage and packing area | 24 | 24 | 75 | 75 | 35
| Milling room | 24 | 24 | 75 | 75 | 35
| Tablet compressing and coating | 24 | 24 | 75 | 75 | 35
| Effervescent tablets and powders | 24 | 24 | 75 | 75 | 20
| Hypodermic tablets | 24 | 24 | 75 | 75 | 30
| Colloids | 21 | 21 | 70 | 70 | 30-50
| Caught drops | 27 | 27 | 80 | 80 | 40
| Glandular products | 24 | 24 | 76 | 76 | 5-10
| Ampoule manufacturing | 24 | 24 | 75 | 75 | 35-50
| Gelatin Capsules | 24 | 24 | 76 | 76 | 35
| Capsule storage | 24 | 24 | 76 | 76 | 35
| Microanalysis | 24 | 24 | 76 | 76 | 50
| Biological manufacturing | 24 | 24 | 76 | 76 | 35
| Liver extracts | 24 | 24 | 76 | 76 | 35
| Serums | 24 | 24 | 76 | 76 | 50
| Animal rooms | 24 | 27 | 75 | 80 | 50
| Small animal rooms | 24 | 26 | 75 | 78 | 50
Paper | Binding, cutting, drying, folding, gluing | 15 | 27 | 59 | 81 | 25-50
| Storage of paper | 15 | 27 | 59 | 81 | 34-45
| Storage of books | 18 | 21 | 64 | 70 | 38-50
Plastics | Manufacturing areas thermosetting molding compounds | 27 | 27 | 80 | 80 | 25-30
| Cellophane wrapping | 24 | 27 | 75 | 80 | 45-65
Photographic | Development of film | 21 | 24 | 70 | 75 | 60
| Drying | 24 | 27 | 75 | 81 | 50
| Printing | 21 | 21 | 70 | 70 | 70
| Cutting | 22 | 22 | 72 | 72 | 65
Plywood | Hot pressing, resin | 32 | 32 | 90 | 90 | 60-70
| Cold pressing | 32 | 32 | 90 | 90 | 15-25
Printing | Binding | 21 | 21 | 70 | 70 | 45
| Folding | 25 | 25 | 77 | 77 | 65
| Pressing, general | 24 | 24 | 75 | 75 | 60-78
| Plate making | 24 | 27 | 75 | 80 | max 45
| Lithographic press room | 24 | 27 | 76 | 80 | 43-47
| Letterpress and web offset rooms | 21 | 27 | 70 | 80 | 50
| Paper storage, letterpress | 21 | 27 | 70 | 80 | 43-47
| Paper storage, multicolor sheet feed lithography | 24 | 27 | 76 | 80 | 50-55
Raw Material Storage | Nuts, insect | 7 | 7 | 45 | 45 | 65-75
| Nuts, rancidity | 1 | 3 | 34 | 38 | 65-75
| Eggs | -1 | -1 | 30 | 30 | 85-90
| Chocolate, flats | 18 | 18 | 65 | 65 | 50
| Butter | -7 | -7 | 20 | 20
| Dates, figs | 4 | 7 | 40 | 45 | 75-65
| Corn Syrup |  |  |  |  | 90-100
| Liquid sugar | 24 | 27 | 75 | 80 | 60-50
Rubber-dipped goods | Cementing | 27 | 27 | 80 | 80 | 25-30
| Dipping surgical articles | 24 | 32 | 75 | 90 | 25-30
| Storage prior to manufacture | 16 | 24 | 60 | 75 | 40-50
| Laboratory, ASTM standard | 24 | 24 | 75 | 75 | 50-55
Textile | Cotton, carding | 24 | 27 | 75 | 81 | 50
| Cotton, spinning | 15 | 27 | 59 | 81 | 60-70
| Cotton, weaving | 20 | 24 | 68 | 75 | 70-80
| Nylon, production | 27 | 27 | 81 | 81 | 50-60
| Rayon, spinning | 21 | 21 | 70 | 70 | 85
| Rayon, twisting | 21 | 21 | 70 | 70 | 65
| Silk, spinning | 24 | 27 | 75 | 81 | 65-70
| Silk, weaving | 24 | 27 | 75 | 81 | 60-70
| Wool, carding | 24 | 27 | 75 | 81 | 65-70
| Wool, spinning | 24 | 27 | 75 | 81 | 55-60
| Wool, weaving | 24 | 27 | 75 | 81 | 50-55
Tobacco | Cigar and cigarette making | 21 | 24 | 70 | 75 | 55-65
| Softening | 32 | 32 | 90 | 90 | 85
| Stemming and strigging | 24 | 30 | 75 | 86 | 70
| Filler tobacco casing conditioning | 24 | 24 | 75 | 75 | 75
| Filler tobacco storage and preparation | 26 | 26 | 78 | 78 | 70
| Wrapper tobacco storage and conditioning | 24 | 24 | 75 | 75 | 75

## airchange
Table 2 : Ventilation requirements in hospitals
Standards | ASHRAE | HTM | Singapore
Room | Minimum no. of air changes/hour
Operating Theatres | 15 | 20 | 20
Intensive Care Unit | 6 | 15 | 15
Wards (airconditioned) | 4 | - | 15
Isolation Ward (air-conditioned) | 6 | - | 15
Table 3 : Design parameters for operating theatres
Design parameters | General | Ultra-clean
1. Temperature | 20±1 °C | 20±1 °C
2. Relative Humidity | 55±5% | 55±5%
3. Bacterial count | <35 cfu/m3 | <10 cfu/m3
4. Supply air velocity at the operating table | 0.38 m/s | 0.38 m/s
5. Fresh air (no recirculation) | 20 air changes/hour | 20 air changes/hour
6. Total number of air changes | 20 air changes/hour | >300 air changes/hour
7. Pressurisation | +25 Pa | +25 Pa
8. Filtration efficiency | 99.997% at terminal | 99.997% at terminal
9. Supply air discharge area | 2.4m x 1.8m | 2.8m x 2.8m
Basement ventilation12 air changes/hr and 30 airchage/hr in case of fire
Air Changes/Hr; Constant Volume v/s VAV Volume System as per dept of Veterans usa
Areas | Minimum Design Supply Air Changes/Hr | Constant Volume (CV) or Variable Air Volume (VAV)
Animal Research Areas | 15 | CV
Ante Rooms | 12 | See Standard Detail 15900-7 or 15900-7A
Autopsy Suite (All rooms) | 12 | CV
Corridors | 4 | VAV
Dark Rooms | 10 | CV
Dialysis Rooms | 6 | CV
Dining Room | 10 | VAV
Examination Rooms | 6 | VAV
Intensive Care Units (ICUs) | 8 | CV
(All Types)
BMT Special Areas, Patient Rooms, Donor Rooms, Recovery Rooms, Medical Preparation Rooms | 18 | CV
Isolation Rooms
Aids Patient Room | 15 | CV
Burn Unit | 15 | CV
Leukemia | 15 | CV
Organ Transplant | 12 | CV
Tuberculosis | 12 | CV
Kitchens | 10 | VAV (See Article 3.12)
Laboratories
Bacteriology | 12 | CV
Biochemistry | 12 | CV
Biosafety | 12 | CV
Cytology | 12 | CV
General | 12 | CV
Histology | 12 | CV
Nuclear Medicine | 12 | CV
Pathology | 12 | CV
Special Chemistry | 12 | CV
Medical Media See Article 3.16
Minor Operating Rooms (0.R.s) (Trauma Rooms) | 12 | CV
Operating Rooms (O.R.s) | 15 (Occupied) | 8 (Unoccupied)
Patient Rooms | 4 | VAV
Recovery Rooms | 8 | CV
SPD | See Article 3.20 | CV
Special Procedure Rooms
Bronchoscopy | 12 | CV
Cardiac Catheterization | 15 | CV
Colonoscopy/EGD | 6 | CV
Cystoscopy | 15 | CV
Endoscopy | 6 | CV
Fluoroscopy | 6 | CV
GI (Gastrointestinal) | 10 | CV
Proctoscopy | 6 | CV
Sigmoidoscopy | 6 | CV
Smoking Area | 12 (Occupied) 6(Unoccupied) | CV with two settings
Storage Areas | 4 | CV
Treatment Room | 6 | VAV
Waiting Room | 6 | CV
Typical Fresh Air Requirements AS PER Blue Star
Application | Smoking | Cfm per person |  | Fresh air changes/Hr
|  | Recommended | Minimum
Apartments | Some | 20 | 15 | 1
Stores | None | 7.5 | 5 | 1
bars | Heavy | 30 | 25 | 3
Restaurants | Considerable | 15 | 12 | 2
Hotel Rooms | Considerable | 20 | 15 | 2
Conference rooms | Considerable | 20 | 15 | 3
Theatres | None | 7.5 | 5 | 3
Banks | Occasional | 10 | 7.5 | 2
Offices | Some | 15 | 10 | 1
Computer rooms | None | 10 | 7.5 | 2
Factories | None | 10 | 7.5 | 2
Fresh Air requirements & Circulation Rates for health care establishments
Type of facility | Fresh air Changes /Hr | Circulation Air Changes / hour
Operating theatre | 5 | 25
Recovery room | 2 | 6
ICU | 2 | 6
Delivery room | 5 | 12
Trauma care | 5 | 12

## noise
Noise Level Recoomendations as per dept of Veterans Washington
Type of Rooms | NC Level
Patient | 35
Examination Room, Endoscopy and Bronchoscopy | 35
Audio Suites, Audio Speech Pathology | 35
Phono/Cardiology | 35
Chapels | 40
Conference | 35
Auditorium, Theaters | 40
Operating Rooms (Major and Minor) | 35
Offices, Small Private | 40
Offices, Large Open | 35
Pharmacy | 40
Lobbies, Waiting Areas | 35
Treatment | 40
Corridors, Nurse Stations | 40
Bathrooms, Toilets | 40
Laboratories | 45
SPD, Dining, Food Service/Serving | 45
Therapeutic Pools | 45
Laundries | 50
Gymnasiums, Recreation Rooms | 50
X-Rays and General Work Rooms | 40
Laundries | 50
All Other Occupied Areas | 35-40*

## air
Temperature, density, specific heat, thermal conductivity, expansion coefficient, kinematic viscosity and Prandtl number for air at temperature between -150oC and 400oC.
Temperature | Density | Specific heat capacity | Thermal conductivity | Kinematic viscosity | Expansion coefficient | Prandtl's number
- t - | - ρ - | - cp - | - l - | ν x06 | b x 103 | Pr
| (kg/m3) | (kJ/kg.K) | (W/m.K) | (m2/s) | (1/K)
(oC)
-150 | 2.793 | 1.026 | 0.0116 | 3.08 | 8.21 | 0.76
-100 | 1.980 | 1.009 | 0.0160 | 5.95 | 5.82 | 0.74
-50 | 1.534 | 1.005 | 0.0204 | 9.55 | 4.51 | 0.725
0 | 1.293 | 1.005 | 0.0243 | 13.30 | 3.67 | 0.715
20 | 1.205 | 1.005 | 0.0257 | 15.11 | 3.43 | 0.713
40 | 1.127 | 1.005 | 0.0271 | 16.97 | 3.20 | 0.711
60 | 1.067 | 1.009 | 0.0285 | 18.90 | 3.00 | 0.709
80 | 1.000 | 1.009 | 0.0299 | 20.94 | 2.83 | 0.708
100 | 0.946 | 1.009 | 0.0314 | 23.06 | 2.68 | 0.703
120 | 0.898 | 1.013 | 0.0328 | 25.23 | 2.55 | 0.70
140 | 0.854 | 1.013 | 0.0343 | 27.55 | 2.43 | 0.695
160 | 0.815 | 1.017 | 0.0358 | 29.85 | 2.32 | 0.69
180 | 0.779 | 1.022 | 0.0372 | 32.29 | 2.21 | 0.69
200 | 0.746 | 1.026 | 0.0386 | 34.63 | 2.11 | 0.685
250 | 0.675 | 1.034 | 0.0421 | 41.17 | 1.91 | 0.68
300 | 0.616 | 1.047 | 0.0454 | 47.85 | 1.75 | 0.68
350 | 0.566 | 1.055 | 0.0485 | 55.05 | 1.61 | 0.68
400 | 0.524 | 1.068 | 0.0515 | 62.53 | 1.49 | 0.68
More about Air Composition!

## hot
Hot water Cons}mption
| Consumption per occupant |  | Peak demand per occupant |  | Storage per occupant
| liter/day | gal/day | liter/hr | gal/hr | lmter | gal
Factories (no process) | 22 - 45 | 38847 | 9 | 2 | 5 | 1
Hospitals, general | 160 | 35 | 30 | 7 | 27 | 6
Hospitals, me.tal | 110 | 25 | 22 | 5 | 27 | 6
Hostels | 90 | 20 | 45 | 10 | 30 | 7
Hotels | 90 - 160 | 00 - 35 | 45 | 10 | 30 | 7
Houses and flats | 90 - 160 | 00 - 35 | 45 | 10 | 30 | 7
Offices | 22 | 5 | 9 | 2 | 5 | 1
Schools, boarding | 115 | 25 | 20 | 4 | 25 | 5
Schools, day | 15 | 3 | 9 | 2 | 5 | 1

## duct
Air Velocity
Type of Duct | Comfort systems | Industrial systems | High speed systems
Main ducts | 4 – 7 m/s | 8 – 12 m/s | 10 – 18 m/s
Main branch ducts | 3 – 5 m/s | 5 – 8 m/s | 6 – 12 m/s
Branch ducts | 1 – 3 m/s | 3 – 5 m/s | 5 – 8 m/s
Equivalent duct sizes for rectangular and circular duct delivering air airflows at different CFM.
CFM | Equivant | Equivant Diameter
(Cubic Feet per Minute) | Rectangular Duct Sizes | Round Duct Sizes
| (Inches) | (Inches)
100 | 3 X 4 | 4
200 | 3 X 7 | 5
4 X 5
300 | 4 X 7 | 6
5 X 6
400 | 4 X 9 | 7
5 X 7
6 X 6
500 | 6 X 7 | 8
750 | 5 X 12 | 9
6 X 10
7 X 8
1000 | 7 X 10 | 10
8 X 9
1250 | 8 X 10 | 10
9 X 9
1500 | 8 X 12 | 12
10 X 10
1750 | 8 X 14 | 12
9 X 12
10 X 11
2000 | 8 X 15 | 12
10 X 12
2500 | 10 X 14 | 14
12 X 12
3000 | 12 X 14 | 14
3500 | 12 X 15 | 15
4000 | 10 X 22 | 16
14 X 15
4500 | 12 X 19 | 17
14 X 16
5000 | 10 X 25 | 17
12 X 20
15 X 16
6000 | 14 X 20 | 19
15 X 18
7000 | 12 X 26 | 20
16 X 20
8000 | 12 X 30 | 21
14 X 25
9000 | 12 X 34 | 22
15 X 25
10000 | 12 X 36 | 23
16 X 25
20 X 20
12500 | 12 X 45 | 24
16 X 30
20 X 24
15000 | 16 X 36 | 26
18 X 30
23 X 25
17500 | 16 X 40 | 28
20 X 32
25 X 25
20000 | 16 X 45 | 30
20 X 35
25 X 28
25000 | 16 X 55 | 32
20 X 43
25 X 38
30000 | 20 X 50 | 34
30 X 32
35000 | 20 X 55 | 36
30 X 35
40000 | 25 X 48 | 38
30 X 40
45000 | 25 X 25 | 40
32 X 40
50000 | 32 X 45 | 42
35 X 40

## effort
Table 1 Metabolic Rates
Activity | Metabolic Rate | Activity | Metabolic Rate
| (Met) |  | (Met)
RESTING | 0.7 | MISCELLANEOUS OCCUPATIONS | 1.4-2.0
Sleeping | 0.8 | Bakery | 1.2-2.4
Reclining | 1.0 | Brewery | 1.8-2.2
Seated, quiet | 1.2 | Carpentry | 4.0-4.8
Standing, relaxed | 2.0-3.8 | Machine sawing, table | 5.6-6.4
WALKING | 2.0-3.4 | Sawing by hand | 3.0-3.4
DOMESTIC WORK, WOMEN | 1.6-2.0 | Planning by hand | 5.0-7.0
House cleaning | 2.0-3.6 | Foundry work | 2.2-3.0
Cooking | 1.4-1.8 | Using a pneumatic hammer | 1.4-1.8
Washing by hand and ironing | 1.2-1.4 | Tending furnaces | 2.0-2.4
Shopping | 1.1-1.3 | Garage work | 3.5-4.5
OFFICE WORK | 1.1-1.3 | General laboratory work | 2.0
Typing | 1.2-2.0 | Machine work | 1.6
Miscellaneous office work | 3.0-4.0 | Light | 1.1
Drafting | 2.4-4.4 | Heavy | 1.5
LEISURE ACTIVITIES | 3.6-4.6 | Shop Assistant | 2.0
Stream fishing | 5.0-7.2 | Teacher | 3.2
Calisthenics exercise | 5.0-7.2 | Watch repairer, seated | 1.4
Dancing, social | 7.0-8.7 | Vehicle driving | 1.8
Tennis, singles | 1.4-2.6 | Car | 2.4
Squash, singles | 1.4-1.8 | Motorcycle
Basketball, half court, intramural |  | Heavy vehicle
Wrestling-competitive or intensive |  | Aircraft flying routine
Golf, swimming and walking |  | Instrument landing
Golf, swinging and golf cart |  | Combat flying

## Sheet1
Fa | Cel | Cel | Fah | Feet | meter
115 | 46.11 | 15 | 59 | 1 | 0.3
110 | 43.33 | 16 | 60.8 | 2 | 0.61
105 | 40.56 | 17 | 62.6 | 3 | 0.91
100 | 37.78 | 18 | 64.4 | 4 | 1.22
95 | 35 | 19 | 66.2 | 5 | 1.52
90 | 32.22 | 20 | 68 | 6 | 1.83
85 | 29.44 | 21 | 69.8 | 7 | 2.13
80 | 26.67 | 22 | 71.6 | 8 | 2.44
75 | 23.89 | 23 | 73.4 | 9 | 2.74
74 | 23.33 | 24 | 75.2 | 10 | 3.05
73 | 22.78 | 25 | 77 | 11 | 3.35
72 | 22.22 | 26 | 78.8
71 | 21.67 | 27 | 80.6
70 | 21.11 | 28 | 82.4
69 | 20.56 | 29 | 84.2
68 | 20 | 30 | 86
67 | 19.44 | 31 | 87.8
66 | 18.89 | 32 | 89.6
65 | 18.33 | 33 | 91.4
64 | 17.78 | 34 | 93.2
63 | 17.22 | 35 | 95
62 | 16.67 | 36 | 96.8
61 | 16.11 | 37 | 98.6
60 | 15.56 | 38 | 100.4
59 | 15 | 39 | 102.2
58 | 14.44 | 40 | 104
|  | 41 | 105.8
|  | 42 | 107.6
|  | 43 | 109.4
|  | 44 | 111.2
|  | 45 | 113

## efficiency
|  | EER | Efficacy | Cond | Evap | Efficiency
|  |  | kw/ton | 0 F | 0 F
1 | Screw Comp | 14-17 | .7-.85 | 100 | 40 | 75-82
| Part load |  | 0.42
| Screw Comp chiller package air cooled | 9 -10 | 1.06-1.15 | 100 | 40
2 | Reciprocating water | 15 | 0.79
| Reci Air cooled | 10.4-11.3 | 1.06-1.15
Recopro chiiler package air
| 20-200 tons | 9-10.9 | 1.1-1.33
| Recopro chiiler package water | 13.1-15.8 | .76-92
Screw type 120 tons carrier make
| size | 3.3 m x1 m x 1.9 m
| Chilled LPM | 1097.65
| Condensing LPM | 1722.175
| motor | 60 kw x 2 star-delta

## rh
Table HVAC 21 : Recommended Relative Humidity
SN | Production and Process Environment | Recommended Relative Humidity - RH (%) | SN | Production and Process Environment | Recommended Relative Humidity - RH (%)
1 | Sugar Storage | 20-35% | 15 | Plastic Pallets | 5-30%
2 | Breweries | 35-45% | 16 | Computer Peripherals | 50-60%
3 | Coffee Powder | 30-40% | 17 | Rust Resistance | Below 40%
4 | Milk Powder Storage | 20-35% | 18 | Medical Syrups | 30-40%
5 | Seed Storage | 35-45% | 19 | Capsule Storage | 30-45%
6 | Unpacked Medicine | 20-35% | 20 | Powder Storage | 30-45%
7 | Transformer Winding | 15-30% | 21 | Wood Drying | 25-35%
8 | Semiconductors | 30-50% | 22 | Explosives | 35-50%
9 | Books and Paper Archive | 40-55% |  |  | Note! lower RH may cause static electricity and sparks ignition
10 | Paper Storage | 35-45% | 23 | Normal Storage | 50-55%
11 | Preventing Rust and Corrosion | below 55%, | 24 | Musical Instrument | 45-55%
|  | < 40% for no rust | 25 | Leather Product | 40-55%
12 | Library | 50-55% | 26 | Cable Wrapping | 15-25%
13 | Spray Paint | 30-50% | 27 | Chemical Laboratory | 30-45%
14 | Laboratory electronics | 45-60%

## occupancy
Occupancy
Type of building | Type of room | m2 area per person
Assembly building | Lecture room | 0,6
| Library | 5
| Cinema | 0,6
| Concert hall | 0,6
| Theatre | 0,6
Hotel | Rooms | 5
| Lobby | 0,6
| Assembly room | 1,5
Kindergarten |  | 38751
Offices | Single office | 10
| Meeting room | 1,5
Restaurant | With service | 1,5
| Without service | 1
Schools | Lecture room | 0,6
| Class room | 2
| Corridor | 2
| Laboratory | 3
Shop | Detail | 2
| Supermarket | 2
Sport | Gymnasium | 1,5
| Swimming pool | 4

## heatgain
Typical Application | Sensible Heat | Latent Heat
| (btu/hr) | (btu/hr)
Theater-Matinee | 200 | 130
Theater-Evening | 215 | 135
Offices, Hotels, Apartments | 215 | 185
Retail & Department Stores | 220 | 230
Drug Store | 220 | 280
Bank | 220 | 280
Restaurant | 240 | 310
Factory | 240 | 510
Dance Hall | 270 | 580
Factory | 330 | 670
Bowling Alley | 510 | 940
Factory | 510 | 940
Tabulated values are based on 78oF for dry-bulb temperature.
Adjusted total heat value for sedentary work, restaurant, includes 60 Btu/hr for food per individual (30 Btu/h sensible and 30 Btu/ latent heat).
For bowling figure one person per alley actually bowling, and all others as sitting (400 Btu/h) or standing (550 Btu/h).
Heat gain from people - watts
Approximate Heat Gain from Occupants in Air Conditioned Spaces.
The table below can be used to estimate the sensible and latent heat from people. The values can be used to calculate the heat load handled by the air condition system.
Degree of Activity | Typical Application | Average Metabolic rate - male adult (W) | Room Dry Bulb Temperature (oC)
|  |  | 28 |  | 27 |  | 26 |  | 24 |  | 22 |  | 20
|  |  | Sens. | Lat. | Sens. | Lat. | Sens. | Lat. | Sens. | Lat. | Sens. | Lat. | Sens. | Lat.
Seated at rest | Cinema, theatre, school | 100 | 50 | 50 | 55 | 45 | 60 | 40 | 67 | 33 | 72 | 28 | 79 | 21
Seated, very light work | Gomputer working | 120 | 50 | 70 | 55 | 65 | 60 | 60 | 70 | 50 | 478 | 42 | 84 | 36
Office work | Hotel reception, cashier | 130 | 50 | 80 | 56 | 74 | 60 | 70 | 70 | 60 | 78 | 52 | 86 | 44
Standing, walking slowly | Laboratory work | 130 | 50 | 80 | 56 | 74 | 60 | 70 | 70 | 60 | 78 | 52 | 86 | 44
Walking, seated |  | 150 | 53 | 97 | 58 | 92 | 64 | 86 | 76 | 74 | 84 | 66 | 90 | 60
Moderate work | Servant, hair dresser | 160 | 55 | 105 | 60 | 100 | 68 | 92 | 80 | 80 | 90 | 70 | 98 | 62
Light bench work | Mechanical production | 220 | 55 | 165 | 52 | 158 | 70 | 150 | 85 | 135 | 100 | 120 | 115 | 105
Moderate Dancing | Party | 250 | 62 | 188 | 70 | 180 | 78 | 172 | 94 | 156 | 110 | 140 | 125 | 125
Fast walking | Mountain walking | 300 | 80 | 220 | 88 | 212 | 96 | 204 | 110 | 190 | 130 | 170 | 145 | 155
Heavy work | Athletics | 430 | 132 | 298 | 138 | 292 | 144 | 286 | 154 | 276 | 170 | 260 | 188 | 242
Heat gain from people - btu/h

## humid
Humidifying Air - SI units
The amount of vapor - kg per cubic meter - in humid air.
The table below can be used to estimate the amount of vapor in an air volume of 100 m3:
Vapor in Air (kg per 100 m3 airflow) | Relative Humidity (%)
Dry Temperature (oC) | 100 | 85 | 80 | 75 | 70 | 65 | 60 | 55 | 50 | 45 | 40 | 35 | 30
32 | 3.39 | 2.89 | 2.72 | 2.55 | 2.38 | 2.19 | 2.04 | 1.93 | 1.7 | 1.53 | 1.36 | 1.19 | 1.02
31 | 3.22 | 2.73 | 2.57 | 2.41 | 2.25 | 2.1 | 1.93 | 1.77 | 1.61 | 1.45 | 1.29 | 1.13 | 0.97
30 | 3.05 | 2.59 | 2.44 | 2.29 | 2.13 | 1.97 | 1.83 | 1.67 | 1.52 | 1.37 | 1.22 | 1.07 | 0.91
29 | 2.89 | 2.45 | 2.31 | 2.17 | 2.02 | 1.88 | 1.73 | 1.59 | 4.45 | 1.3 | 1.16 | 1.01 | 0.87
28 | 2.73 | 2.32 | 2.19 | 2.05 | 1.91 | 1.78 | 1.64 | 1.5 | 1.37 | 1.23 | 1.1 | 0.96 | 0.82
27 | 2.59 | 2.2 | 2.07 | 1.94 | 1.81 | 1.68 | 1.55 | 1.42 | 1.29 | 1.16 | 1.03 | 0.91 | 0.78
26 | 2.45 | 2.08 | 1.96 | 1.83 | 1.71 | 1.59 | 1.47 | 1.34 | 1.22 | 1.1 | 0.97 | 0.86 | 0.73
25 | 2.31 | 1.97 | 1.85 | 1.73 | 1.62 | 1.5 | 1.39 | 1.27 | 1.16 | 1.04 | 0.93 | 0.81 | 0.69
24 | 2.19 | 1.86 | 1.75 | 1.64 | 1.53 | 1.42 | 1.31 | 1.2 | 1.09 | 0.98 | 0.87 | 0.77 | 0.66
23 | 2.06 | 1.76 | 1.63 | 1.55 | 1.45 | 1.34 | 1.24 | 1.14 | 1.03 | 0.93 | 0.83 | 0.72 | 0.62
22 | 1.95 | 1.66 | 1.56 | 1.46 | 1.36 | 1.27 | 1.17 | 1.07 | 0.98 | 0.88 | 0.78 | 0.68 | 0.59
21 | 1.84 | 1.56 | 1.47 | 1.38 | 1.29 | 1.2 | 1.1 | 1.02 | 0.92 | 0.83 | 0.74 | 0.67 | 0.55
20 | 1.74 | 1.48 | 1.39 | 1.3 | 1.22 | 1.13 | 1.04 | 0.98 | 0.87 | 0.78 | 0.69 | 0.61 | 0.52
19 | 1.63 | 1.39 | 1.31 | 1.23 | 1.15 | 1.06 | 0.98 | 0.9 | 0.82 | 0.74 | 0.65 | 0.57 | 0.49
18 | 1.54 | 1.31 | 1.24 | 1.16 | 1.08 | 1 | 0.93 | 0.85 | 0.77 | 0.69 | 0.62 | 0.54 | 0.46
17 | 1.45 | 1.24 | 1.16 | 1.09 | 1.02 | 0.94 | 0.87 | 0.8 | 0.73 | 0.65 | 0.59 | 0.51 | 0.44
15 | 1.29 | 1.1 | 1.03 | 0.97 | 0.9 | 0.84 | 0.77 | 0.71 | 0.66 | 0.58 | 0.52 | 0.45 | 0.39
10 | 0.94 | 0.8 | 0.76 | 0.71 | 0.66 | 0.61 | 0.57 | 0.52 | 0.47 | 0.43 | 0.38 | 0.33 | 0.28
0 | 0.49 | 0.41 | 0.39 | 0.37 | 0.34 | 0.32 | 0.29 | 0.27 | 0.24 | 0.22 | 0.2 | 0.17 | 0.15
-5 | 0.33 | 0.28 | 0.26 | 0.25 | 0.23 | 0.21 | 0.2 | 0.18 | 0.16 | 0.15 | 0.13 | 0.11 | 0.1
-10 | 0.22 | 0.18 | 0.17 | 0.16 | 0.15 | 0.14 | 0.13 | 0.12 | 0.11 | 0.1 | 0.09 | 0.08 | 0.06
Note! In psychrometric charts and Mollier diagram the amount of vapor is given in kg/kg dry air. The values from the table above can be transformed dividing by the air density at the actual temperature.
Example - Humidifying Air with Steam
Air at 20oC and 30% relative humidity are humidified to 20oC and 80% relative humidity.
From a table above air at 20oC and 30% relative humidity contains 0.52 kg water vapor per 100 m3 air flow. Air at 20oC and 80% relative humidity contains 1.39 kg per 100 m3 air flow.
The amount of water vapor needed can be calculated as:
Amount of Water Vapor = ((1.39 kg) - (0.52 kg))
= 0.87 kg is the amount of water vapor necessary for an air volume of 100 m3.

## water
[5 empty] | Type of Fitting | Consumption
[6 empty] | liter/h | gal/h
[5 empty] | Basin (private) | 14 | 3
| Type of fitting | Storage Capacity |  |  | Basin (public) | 45 | 10
|  | liters | gal |  | Shower | 180 | 40
| Basin | 90 | 20 |  | Sink | 45-90 | 10-20
| Bath | 900 | 200 |  | Bath | 90-180 | 20-40
| Garden watering tap | 180 | 40
| Shower | 450 - 900 | 100 - 200
| Sink | 90 | 20
| Urinal | 180 | 40
| WC | 180 | 40
below can be used to determine the maximum numbers of draw offs served by a pipe:
Nominal bore of pipe |  |  | Maximum number of draw offs served
|  |  | Flow pipes |  | Return pipes
in | Steel pipe | Copper pipe | Head up to 20 m | Head over 20 m
| (mm) | (mm) | (70 ft) | (70 ft)
1/2 | 15 | 15 | 1 | 1 - 2 | 1 - 8
3/4 | 20 | 22 | 2 - 4 | 3 - 9 | 9 - 29
1 | 25 | 28 | 5 - 8 | 10 - 19 | 30 - 66
1 1/4 | 32 | 35 | 9 - 24 | 20 - 49 | 67 - 169
1 1/2 | 40 | 42 | 25 - 49 | 50 - 79 | 170 - 350
2 | 50 | 54 | 50 - 99 | 80 - 153
2 1/2 | 65 | 67 | 100 - 200 | 154 - 300
Basins, Zinks, showers and similar are regarded as 1 draw off
Baths and similar are regarded as 2 draw offs

## fan
Fan discharge velocities for quiet operation
Application | Supply | Extract
| systems | systems
| m/s | m/s
Sound studios, churches, libraries | 4-5 | 5-7
Cinemas, theatres, ballrooms | 5 - 7,5 | 6-8
Restaurants, offices, hotels, shops | 6-8 | 7-9

## ref
Refrigerant | Formula | Boiling temperature | Critical temperature | Properties | Applications
|  | oC | oC
Ammonia | NH3 | -33 | 133 | Penetrating odour, soluble in water. harmless in concentration up to 1/30%, non flammable, explosive | Large industrial plants
R12 | C Cl2F2 | -29,8 | 112 | Little odour, colourlessas gass or liquid, non flammable, non corrosive of ordinary metals, stable | Small plants with reciprocating compressors.
R11 | C Cl3F | 8,9 | 198 | Non flammable, non corrosive non toxic, stable | Commercial plants with centrifugal compressors.
R22 | CH Cl F2 | -40,8 | 96 | Little odour, colourless as gas or liquid, non toxic, non irritating, non flammable, non corrosive, stable | Packaged airconditioning units where size of equipment and economy are important.
R500 | C Cl2 F2 (73,8%) | -33 |  | Simmilar to R12 | Offers aprox. 20% more refrigeration capacity than R12 for same compressor.
CH3 CH F2 (26.2%)
R502 | C Cl F2 (48,8%) | -45,6 | 90,1 | Non flammable, non toxic, non corrosive, stable | Capacity comparable to R22.
C Cl
F2 - CF3 (51.2%)

## fresh
Minimum Outdoor Air Requirements
Rooms | Outdoor Air
2 Air Changes/Hr, or 10 Air Changes/Hr of Make-up Air for the Adjoining Toilets/ Bathrooms, or 0.85 Cu M/Min (30 CFM) Per Patient.
Patient Bedrooms
Offices (Private) | 1 Air Change/Hr, or 0.56 Cu M/Min (20 CFM) Per Person.
Lounge/Waiting Areas | 0.42 Cu M/Min (15 CFM) Per Person.

## filter
Filter Efficiencies (percent) for all Air systems
Area Served | Pre-filters (Efficiency) | After-filters
(Efficiency)
Animal Holding Areas | 30 | 85
Animal Operating Rooms | 30 | 95
Administrative areas, conference rooms, and lobbies | 15 | 60
Auditoriums, Chapels, and Theaters | 15 | 60
Autopsy Suite exhaust | 30 | 99.97; HEPA Filters
Autopsy Suites supply air | 30 | 85
BMT Suites | 30 | 99.97; HEPA Filters
Burn Unit | 30 | 99.97; HEPA Filters
Clean supplies and processing areas | 30 | 85
Dental Clinics | 30 | 85
Dialysis Rooms | 30 | 85
Dietetics (Kitchen and Dining areas) | 15 | 60
Emergency Care Units (Ambulatory Care} | 30 | 85
Gymnasium | 15 | 60
Heat recovery Units (In exhaust air on upstream side of the coil) | 30 | -
Human Immunodeficiency Virus (HIV) | 30 | 99.97; HEPA Filters
ICUs utilizing return air system | 30 | 99.97; HEPA Filter
ICUs and Recovery Rooms in surgical suite | 30 | 95
Isolation Room exhausts. For TB isolation, see Article 3.22 | 30 | 99.97; HEPA Filters
Laboratories, supply system | 30 | 85
Laundries, soiled holding areas, and bulk storage | 30 | -
MRI, CT Scanners, and Linear Accelerators | 30 | 85
Nuclear Medicine | 30 | 85
Operating Rooms, and Trauma rooms | 30 | 95
Orthopedic Surgery | 30 | 99.97; HEPA Filters
Medical Media | 30 | 85
Make-up units for lab and kitchen range hood | 30 | -
Patient Bed Rooms | 30 | 85
Patient care such as examination, and treatment areas. | 30 | 85
Pharmacy | 30 | 85
Radiation Therapy | 30 | 85
Radiology | 30 | 85
Special Procedure Rooms | 30 | 85
Spinal Card Injury Unit (SCIU) | 30 | 85
SPD | 30 | 85
Warehouses | 30 | -

## exhaust
Minimum Exhaust Air Requirements/Room Pressure
Areas | Room | Exhaust Air
| Pressure | Air Changes/Hr
Admitting and Waiting Areas | Negative | SA + 15 Percent of SA
Ambulance Entrance | Negative | 10
Animal Research | Negative | SA + 15 Percent of SA
Ante Rooms | See Standard Detail 15900-7 or 15900-7A
Autopsy Suite (All Rooms) | Negative | SA + 15 Percent of SA
Battery Charging Areas | Negative | 8
Bathing Facilities | Negative | 10
Bathrooms | Negative | 10
BMT Patient Areas | Positive | SA – 15 Percent of SA
Ceramics Rooms (dental Prosthetics Laboratories) | Positive | SA – 15 Percent of SA
Clean and Preparation Rooms (SPD Suites) | Positive | SA – 15 Percent of SA
Clean Rooms (Laundry Facilities) | Positive | SA – 15 Percent of SA
Dark Rooms | Negative | SA + 15 Percent of SA
Detergent Storage | Negative | SA + 15 Percent of SA
Dialysis | Positive | SA – 15 Percent OF SA
Dietetics {See Note (a)} | Negative | SA + 15 Percent of SA
Enema or Hopper Rooms | Negative | 15
Examination Rooms (MRI Suites) | Equal | 12
Flammable Storage | Negative | 0.3 Cu M/Min/0.1 Sq M, 4.2 Cu M/Min Minimum (1.0 CFM/Sq Ft, 150 CFM Minimum)
Gas Storage | Negative | 0.3 Cu M/Min/0.1 Sq M, 4.2 Cu M/Min Minimum (1.0 CFM/Sq Ft, 150 CFM Minimum)
Glass and Cage Washing Areas | Negative | See Notes
Instrument Rooms (Sterile) | Positive | SA – 15 Percent of SA
Intensive Care Units (ICUs) | Positive | SA – 15 Percent of SA See Article 3.10
Isolation Rooms (Negative Pressure) | See VA STD Detail 15900-7 | SA + 15 Percent of SA
(All Articles listed in Table 3-5 and Table 3-6) and paragraph 2.11.6
Isolation Rooms (Positive Pressure) | See VA STD Detail 15900-7A
Aids Patient Rooms | Positive | SA – 15 Percent of SA
Burn Units | Positive | SA – 15 Percent of SA
Leukemia Patient Rooms | Positive | SA – 15 Percent of SA
Organ Transplant Rooms | Positive | SA – 15 Percent of SA
Janitor Closet (HAC) | Negative | 10
Kitchen (See Note b) | Negative | SA + 15 Percent of SA
Laboratories | Negative | SA + 15 Percent of SA See Article 3.13
Laundry (Central Facility) | Negative | See Article 3.14
Locker Rooms {See Note (c)} | Negative | SA + 15 Percent
See Note (c)
Medical Media Service (MMS) See Article 3.16
Minor Operating Rooms (O.R.s) (Trauma Rooms) | Positive | See Article 3.1.2
Operating Rooms (Surgery Suites) | Positive | See Article 3.21
Oral Surgery and Treatment | Positive | SA – 15 Percent of SA
Radiation Therapy | Negative | SA + 15 Percent of SA
Reagent Grade Water Treatment Rooms | Negative | 8
Recovery Rooms | Positive | SA – 15 Percent of SA
Silver Recovery Rooms | Negative | 6
Smoking Area | Negative | 12
Soiled Dishwashing Rooms | Negative | 6
Soiled Linen Rooms | Negative | 6
Soiled Utility Rooms | Negative | 6
Special Procedure Rooms
Bronchoscopy | Negative | SA + 15 Percent of SA
Cardiac Catheterization | Positive | SA – 15 Percent of SA
Colonoscopy/EGD | Negative | SA + 15 Percent of SA
Cystoscopy | Positive | SA – 15 Percent of SA
Endoscopy | Negative | SA + 15 Percent of SA
Fluoroscopy | Negative | SA + 15 Percent of SA
GI (Gastrointestinal) | Negative | SA + 15 Percent of SA
Proctoscopy | Negative | SA + 15 Percent of SA
Sigmoidoscopy | Negative | SA + 15 Percent of SA
Sterile Corridors (Surgery Suites) See Article 3.21
Storage Rooms (Soiled or Dirty) | Negative | SA + 15 Percent of SA
Tissue Culture Rooms | Positive | SA – 15 Percent of SA
Toilets | Negative | 10
Treatment Room (Bronchoscopy) | Negative | SA + 15 Percent of SA
Trash Collection Areas | Negative | 10
Vestibules | Positive | SA – 15 Percent of SA
Waiting Rooms | Negative | SA + 15 Percent of SA