## airchange
Table HVAC 4(a): Typical Fresh Air Requirements AS PER Blue Star
SN | Application | Smoking | Cfm per person |  | Fresh air changes/Hr
|  |  | Recommended | Minimum
1 | Apartments | Some | 20 | 15 | 1
2 | Stores | None | 7.5 | 5 | 1
3 | bars | Heavy | 30 | 25 | 3
4 | Restaurants | Considerable | 15 | 12 | 2
5 | Hotel Rooms | Considerable | 20 | 15 | 2
6 | Conference rooms | Considerable | 20 | 15 | 3
7 | Theatres | None | 7.5 | 5 | 3
8 | Banks | Occasional | 10 | 7.5 | 2
9 | Offices | Some | 15 | 10 | 1
10 | Computer rooms | None | 10 | 7.5 | 2
11 | Factories | None | 10 | 7.5 | 2
Table 4(b) : Air Changes/Hr; Constant Volume v/s VAV Volume System as per dept of Veterans USA
| Areas | Minimum Design Supply Air Changes/Hr | Constant Volume (CV) or Variable Air Volume (VAV)
| Animal Research Areas | 15 | CV
| Ante Rooms | 12 | See Standard Detail 15900-7 or 15900-7A
| Autopsy Suite (All rooms) | 12 | CV
| Corridors | 4 | VAV
| Dark Rooms | 10 | CV
| Dialysis Rooms | 6 | CV
| Dining Room | 10 | VAV
| Examination Rooms | 6 | VAV
| Intensive Care Units (ICUs) | 8 | CV
(All Types)
| BMT Special Areas, Patient Rooms, Donor Rooms, Recovery Rooms, Medical Preparation Rooms | 18 | CV
Isolation Rooms
| Aids Patient Room | 15 | CV
| Burn Unit | 15 | CV
| Leukemia | 15 | CV
| Organ Transplant | 12 | CV
| Tuberculosis | 12 | CV
| Kitchens | 10 | VAV (See Article 3.12)
Laboratories
| Bacteriology | 12 | CV
| Biochemistry | 12 | CV
| Biosafety | 12 | CV
| Cytology | 12 | CV
| General | 12 | CV
| Histology | 12 | CV
| Nuclear Medicine | 12 | CV
| Pathology | 12 | CV
| Special Chemistry | 12 | CV
Medical Media See Article 3.16
| Minor Operating Rooms (0.R.s) (Trauma Rooms) | 12 | CV
| Operating Rooms (O.R.s) | 15 (Occupied) | 8 (Unoccupied)
| Patient Rooms | 4 | VAV
| Recovery Rooms | 8 | CV
| SPD | See Article 3.20 | CV
Special Procedure Rooms
| Bronchoscopy | 12 | CV
| Cardiac Catheterization | 15 | CV
| Colonoscopy/EGD | 6 | CV
| Cystoscopy | 15 | CV
| Endoscopy | 6 | CV
| Fluoroscopy | 6 | CV
| GI (Gastrointestinal) | 10 | CV
| Proctoscopy | 6 | CV
| Sigmoidoscopy | 6 | CV
| Smoking Area | 12 (Occupied) 6(Unoccupied) | CV with two settings
| Storage Areas | 4 | CV
| Treatment Room | 6 | VAV
| Waiting Room | 6 | CV
Table 4(c) : Ventilation requirements in hospitals
| Standards | ASHRAE | HTM | Singapore
| Room | Minimum no. of air changes/hour
| Operating Theatres | 15 | 20 | 20
| Intensive Care Unit | 6 | 15 | 15
| Wards (airconditioned) | 4 | - | 15
| Isolation Ward (air-conditioned) | 6 | - | 15
Table 4(d) : Design Parameters for Operating Theatres
| Design parameters | General | Ultra-clean
| 1. Temperature | 20±1 °C | 20±1 °C
| 2. Relative Humidity | 55±5% | 55±5%
| 3. Bacterial count | <35 cfu/m3 | <10 cfu/m3
| 4. Supply air velocity at the operating table | 0.38 m/s | 0.38 m/s
| 5. Fresh air (no recirculation) | 20 air changes/hour | 20 air changes/hour
| 6. Total number of air changes | 20 air changes/hour | >300 air changes/hour
| 7. Pressurisation | +25 Pa | +25 Pa
| 8. Filtration efficiency | 99.997% at terminal | 99.997% at terminal
| 9. Supply air discharge area | 2.4m x 1.8m | 2.8m x 2.8m
Table 4 (e) : Fresh Air requirements & Circulation Rates for health care establishments
| Type of facility | Fresh air Changes /Hr | Circulation Air Changes / hour
| Operating theatre | 5 | 25
| Recovery room | 2 | 6
| ICU | 2 | 6
| Delivery room | 5 | 12
| Trauma care | 5 | 12
Basement ventilation12 air changes/hr and 30 airchage/hr in case of fire